Sprinkler Inspection Certificate
For
	560 W. Mitchell St MOB		
	560 W. Mitchell Street		
	Suite 202		
	Petoskey, MI 49770		
Tested to NFPA 25 Standards
This Inspection was performed in accordance with applicable NFPA Standards.  The subsequent pages of this report provide performance measurements, listed ranges of acceptable results, and complete documentation of the inspection.  Whenever discrepancies exist between acceptable performance standards and actual test results, notes and/or recommended solutions have been proposed or provided for immediate review and approval.
Annual Inspection
Inspection Date
Sep 28, 2022
Building: 560 W. Mitchell St MOB	Company: Vanguard Fire & Security Systems, Inc.	
Contact: Brian Lepird	Contact: Jason Johnston	
Title: Site Contact	Title: Service Technician	

Executive Summary
Generated by: BuildingReports.com

Building Information	
  Building: 560 W. Mitchell St MOB	Contact: Brian Lepird	
  Address: 560 W. Mitchell Street	Phone: 231-330-3225	
  Address: Suite 202	Fax: 	
  City/State/ZIP Code: Petoskey, MI 49770	Mobile: 	
  Country: United States of America	Email: blepird@landmarkleadership.com	
Inspection Performed By	
  Company: Vanguard Fire & Security Systems, Inc.	Inspector: Jason Johnston	
  Address: 2101 Martindale SW	Phone: 616-245-8719	
  Address: 	Fax: 	
  City/State/ZIP Code: Grand Rapids, MI 49509	Mobile: 	
  Country: United States of America	Email: service@vanguard-fire.com	
System Control Unit	
System Type	System Location	Protected Area	Devices	
  Wet Pipe	  	  Staircase A	  1	
  Wet Pipe	  	  Staircase B	  1	
  Wet Pipe	  	  Staircase C	  1	
  Wet Pipe	  1st floor	  Area-staircase B	  1	
  Wet Pipe	  1st floor	  Area-staircase b	  1	
  Wet Pipe	  1st floor	  Area-staircase c	  2	
  Wet Pipe	  2nd floor	  Area-staircase B	  4	
  Wet Pipe	  2nd floor	  Area-staircase C	  2	
  Wet Pipe	  3rd floor	  Area-staircase B	  3	
  Wet Pipe	  3rd floor	  Area-staircase c	  3	
  Wet Pipe	  4th floor	  Area-staircase B	  4	
  Wet Pipe	  4th floor	  Area-staircase C	  2	
  Wet Pipe	  5th floor	  Area-staircase B	  5	
  Wet Pipe	  5th floor	  Area-staircase C	  1	
  Wet Pipe	  5th floor	  Staff Elevator	  1	
  Wet Pipe	  Basement	  Area	  1	
  Wet Pipe	  Building-	  Building-	  1	
  Wet Pipe	  Penthouse	  	  6	
  Wet Pipe	  main floor	  Area- outside main riser roo	  7	
  Wet Pipe	  main floor	  Area-staircase A	  3	
  Wet Pipe	  main floor	  Area-staircase B	  19	
  Wet Pipe	  main floor	  Area-staircase C	  1	
  Wet Pipe	  main floor	  Area-staircase c	  2	

Inspection Summary	
Category	Total Items	Serviced	Passed	Failed/Other	
	Qty	%	Qty	%	Qty	%	Qty	%	
  Alarm	13	18.06%	13	100.00%	13	100.00%	0	0.00%	
  Device	13	18.06%	13	100.00%	13	100.00%	0	0.00%	
  Hose	4	5.56%	4	100.00%	4	100.00%	0	0.00%	
  Sprinkler	6	8.33%	6	100.00%	6	100.00%	0	0.00%	
  Valve	36	50.00%	36	100.00%	36	100.00%	0	0.00%	
Totals	72	100%	72	100.00%	72	100.00%	0	0.00%	

Certification	
Company: Vanguard Fire & Security Systems, Inc.	Building: 560 W. Mitchell St MOB	
Inspector: Jason Johnston	Contact: Brian Lepird	
		
Signed: Sep 29, 2022	Signed: 	

Jason Johnston Certifications	
Certification Type	Number	
ABPA Backflow Assembly Tester	35915	

Inspection & Testing
Generated by: BuildingReports.com

Building: 560 W. Mitchell St MOB	
The Inspection & Testing section lists all of the items inspected in your building.  Items are grouped by Passed or Failed/Other. Items are listed by Category. Each item includes the services performed, and the time & date at which testing occurred.	

Device Type	Location	Service	Time	Date	
Passed	
Wet Pipe, Staircase A	
Standpipe	Basement - 6 East Stairwell A	Annual	11:49:28 AM	09/28/2022	
Wet Pipe, Staircase B	
Standpipe	Basement - 5 East Stairwell B	Annual	11:49:32 AM	09/28/2022	
Wet Pipe, Staircase C	
Standpipe	Basement - E East Stairwell C	Annual	11:49:36 AM	09/28/2022	
1st floor Wet Pipe, Area-staircase B	
Control Valve	1st Inside Stairwell B	Annual	11:32:45 AM	09/28/2022	
1st floor Wet Pipe, Area-staircase b	
Waterflow Switch	1st Inside Stairwell B	Annual	11:32:54 AM	09/28/2022	
1st floor Wet Pipe, Area-staircase c	
Gauge	1st Staff Elevator Closet	Annual	11:35:48 AM	09/28/2022	
Inspector's Test	1st Staff Elevator Closet	Annual	11:35:54 AM	09/28/2022	
2nd floor Wet Pipe, Area-staircase B	
Waterflow Switch	2nd Inside Stairwell B	Annual	11:30:49 AM	09/28/2022	
Gauge	2nd Staff Elevator Closet	Annual	11:26:48 AM	09/28/2022	
Control Valve	2nd Inside Stairwell B	Annual	11:30:24 AM	09/28/2022	
Inspector's Test	2nd Staff Elevator Closet	Annual	11:26:54 AM	09/28/2022	
2nd floor Wet Pipe, Area-staircase C	
Waterflow Switch	2nd Inside Stairwell C	Annual	11:24:37 AM	09/28/2022	
Control Valve	2nd Inside Stairwell C	Annual	11:24:32 AM	09/28/2022	
3rd floor Wet Pipe, Area-staircase B	
Waterflow Switch	3rd Inside Stairwell B	Annual	11:15:01 AM	09/28/2022	
Waterflow Switch	3rd Above Ceiling Stairwell C	Annual	12:02:35 PM	09/28/2022	
Control Valve	3rd Inside Stairwell B	Annual	11:13:51 AM	09/28/2022	
3rd floor Wet Pipe, Area-staircase c	
Gauge	3rd Staff Elevator Closet	Annual	11:17:28 AM	09/28/2022	
Control Valve	3rd Inside Stairwell C	Annual	11:22:35 AM	09/28/2022	
Inspector's Test	3rd Staff Elevator Closet	Annual	11:19:39 AM	09/28/2022	
4th floor Wet Pipe, Area-staircase B	
Waterflow Switch	4th Above Ceiling Stairwell B	Annual	11:10:24 AM	09/28/2022	
Gauge	4th Staff Elevator Closet	Annual	11:06:30 AM	09/28/2022	
Control Valve	4th Above Ceiling Stairwell B	Annual	11:10:20 AM	09/28/2022	
Inspector's Test	4th Staff Elevator Closet	Annual	11:06:36 AM	09/28/2022	
4th floor Wet Pipe, Area-staircase C	
Waterflow Switch	4th Above Ceiling Stairwell C	Annual	11:04:13 AM	09/28/2022	
Control Valve	4th Above Ceiling Stairwell C	Annual	11:04:05 AM	09/28/2022	
5th floor Wet Pipe, Area-staircase B	
Waterflow Switch	5th Above Ceiling Stairwell B	Annual	10:59:09 AM	09/28/2022	
Gauge	5th Staff Elevator Closet	Annual	10:55:25 AM	09/28/2022	
Gauge	5th Above Ceiling in Stairwell C	Annual	12:14:12 PM	09/28/2022	
Gauge	5th Above Ceiling in Stairwell B	Annual	12:14:19 PM	09/28/2022	
Control Valve	5th Above Ceiling Stairwell B	Annual	10:59:04 AM	09/28/2022	
5th floor Wet Pipe, Area-staircase C	
Waterflow Switch	5th Above Ceiling Stairwell C	Annual	11:02:36 AM	09/28/2022	
5th floor Wet Pipe, Staff Elevator	
Inspector's Test	5th Staff Elevator Closet	Annual	10:55:35 AM	09/28/2022	
Basement Wet Pipe, Area	
Control Valve	5th Above Ceiling Gastro Nurse Station	Annual	12:14:25 PM	09/28/2022	
Building- Wet Pipe, Building-	
Piping	Basement Internal Piping	Annual	12:02:13 PM	09/28/2022	
Penthouse Wet Pipe	
Waterflow Switch	Penthouse	Annual	10:49:19 AM	09/28/2022	
Gauge	Penthouse	Annual	10:49:15 AM	09/28/2022	
Gauge	Penthouse Top of penthouse stairs	Annual	10:53:17 AM	09/28/2022	
Control Valve	Penthouse	Annual	10:49:34 AM	09/28/2022	
Control Valve	Penthouse	Annual	10:53:08 AM	09/28/2022	
Inspector's Test	Penthouse	Annual	10:50:03 AM	09/28/2022	
main floor Wet Pipe, Area- outside main riser roo	
Waterflow Switch	Basement Outside riser room	Annual	12:14:44 PM	09/28/2022	
Fire Dep't Connection	Basement Riser rm	Annual	12:02:10 PM	09/28/2022	
Sprinkler Box	Basement Riser room	Annual	11:49:39 AM	09/28/2022	
Sprinkler Box	Basement Riser room	Annual	11:49:43 AM	09/28/2022	
Sprinkler Box Spares	Basement Riser room	Annual	11:49:51 AM	09/28/2022	
Sprinkler Box Spares	Basement Riser room	Annual	11:49:53 AM	09/28/2022	
Sprinkler Box Spares	Basement Riser room	Annual	11:49:56 AM	09/28/2022	
main floor Wet Pipe, Area-staircase A	
Waterflow Switch	Basement Inside Stairwell A	Annual	12:14:57 PM	09/28/2022	
Control Valve	Basement Inside Hospital Storage	Annual	12:14:40 PM	09/28/2022	
Control Valve	Basement Inside Stairwell A	Annual	12:15:08 PM	09/28/2022	
main floor Wet Pipe, Area-staircase B	
Pressure Switch	Basement Riser room	Annual	11:50:17 AM	09/28/2022	
Drain	Basement Riser 
room	Annual	12:00:19 PM	09/28/2022	
Gauge	Basement Closet beside Stairwell A	Annual	11:45:33 AM	09/28/2022	
Gauge	Basement Riser 
room	Annual	11:50:24 AM	09/28/2022	
Gauge	Basement Riser 
room	Annual	12:00:12 PM	09/28/2022	
Backflow Prevention	Basement Riser rm tested 3/12/22 by other vendor	Visually Checked	12:16:04 PM	09/28/2022	
Check Valve	Basement Riser 
room	Annual	12:02:04 PM	09/28/2022	
Check Valve	Basement Riser room	Annual	12:02:24 PM	09/28/2022	
Check Valve	Basement Inside Stairwell A	Annual	12:15:24 PM	09/28/2022	
Check Valve	1st Inside Stairwell B	Annual	11:32:28 AM	09/28/2022	
Check Valve	2nd Inside Stairwell C	Annual	11:23:50 AM	09/28/2022	
Check Valve	2nd Inside Stairwell B Riser 
room	Annual	11:30:28 AM	09/28/2022	
Check Valve	3rd Inside Stairwell B	Annual	11:13:58 AM	09/28/2022	
Check Valve	3rd Inside Stairwell C	Annual	11:22:23 AM	09/28/2022	
Control Valve	Basement Riser room	Annual	11:50:07 AM	09/28/2022	
Control Valve	Basement Riser room	Annual	11:56:23 AM	09/28/2022	
Control Valve	Basement Riser room	Annual	11:56:43 AM	09/28/2022	
Control Valve	Basement Riser room	Annual	12:15:29 PM	09/28/2022	
Inspector's Test	Basement Closet Beside Stairwell A	Annual	11:45:39 AM	09/28/2022	
main floor Wet Pipe, Area-staircase C	
Control Valve	Basement Above Ceiling Stairwell C	Annual	11:40:34 AM	09/28/2022	
main floor Wet Pipe, Area-staircase c	
Control Valve	Basement Above Ceiling Stairwell A	Annual	12:15:12 PM	09/28/2022	
Control Valve	5th Above Ceiling Stairwell C	Annual	11:02:13 AM	09/28/2022	

Wet Pipe Fire Sprinkler Systems
Generated by: BuildingReports.com

Building: 560 W. Mitchell St MOB	1st floor, Area-staircase B	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Alenco		1st Inside Stairwell B	2.5"			þ	20459105	
Description	
Isolation	

Building: 560 W. Mitchell St MOB	1st floor, Area-staircase b	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	Potter Electric	VSR-D	30 sec	2.5	1	þ	20459104	

Building: 560 W. Mitchell St MOB	1st floor, Area-staircase c	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Components	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
AGF	1000	90	36		þ	18121699	
Location	
1st Staff Elevator Closet	
Devices	
Gauge	
Location	Service Date	
1st Staff Elevator Closet	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Argco	SG3	90	Water	1/4	þ	36606920	

Building: 560 W. Mitchell St MOB	2nd floor, Area-staircase B	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	Potter Electric	VSR-F	30 sec	2.5	1	þ	20459101	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Ball	Alenco		2nd Inside Stairwell B	2.5"			þ	20459102	
Description	
Isolation	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
G/J Innovations Inc	52S1	80	42		þ	18121700	
Location	
2nd Staff Elevator Closet	
Devices	
Gauge	
Location	Service Date	
2nd Staff Elevator Closet	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Argco	SG3	90	Water	1/4	þ	36606921	

Building: 560 W. Mitchell St MOB	2nd floor, Area-staircase C	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	Potter Electric	VSR-F	30 sec	2.5	1	þ	20459090	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Alenco	BFV	2nd Inside Stairwell C	2.5"			þ	20459089	
Description	
Isolation	

Building: 560 W. Mitchell St MOB	3rd floor, Area-staircase B	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor	WFD-25	30 sec	2.5	1	þ	20459098	
Vane	System Sensor	WFD-25	30 sec	2.5	1	þ	20459088	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Ball	American		3rd Inside Stairwell B	2.5"			þ	20459099	
Description	
Isolation	

Building: 560 W. Mitchell St MOB	3rd floor, Area-staircase c	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	American		3rd Inside Stairwell C	2.5"			þ	20459087	
Description	
Isolation	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
G/J Innovations Inc	52S1	70	38		þ	18121701	
Location	
3rd Staff Elevator Closet	
Devices	
Gauge	
Location	Service Date	
3rd Staff Elevator Closet	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Argco	SG3	90	Water	1/4	þ	36606922	

Building: 560 W. Mitchell St MOB	4th floor, Area-staircase B	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor		30 sec	2.5	1	þ	36606521	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Milwaukee	BB-SCS	4th Above Ceiling Stairwell B	2.5"			þ	36606520	
Description	
Isolation	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
AGF	1000	70	36		þ	18121702	
Location	
4th Staff Elevator Closet	
Devices	
Gauge	
Location	Service Date	
4th Staff Elevator Closet	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Argco	SG3	95	Water	1/4	þ	36606923	

Building: 560 W. Mitchell St MOB	4th floor, Area-staircase C	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor	WFD-25	30 sec	2.5	1	þ	20459085	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Ball	Milwaukee	BB-SOSO	4th Above Ceiling Stairwell C	2.5"			þ	20459084	
Description	
Isolation	

Building: 560 W. Mitchell St MOB	5th floor, Area-staircase B	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor		30 sec	2.5	1	þ	36606523	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Ball	Milwaukee		5th Above Ceiling Stairwell B	2.5"			þ	36606522	
Description	
Isolation	
Devices	
Gauge	
Location	Service Date	
5th Staff Elevator Closet	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	American	SG3	90			þ	36606924	
Gauge	
Location	Service Date	
5th Above Ceiling in Stairwell C	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Argco	SG3	75	Water	1/4	þ	38839442	
Gauge	
Location	Service Date	
5th Above Ceiling in Stairwell B	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Argco	SG3	75	Water	1/4	þ	38839443	

Building: 560 W. Mitchell St MOB	5th floor, Area-staircase C	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor	WFD-25	30 sec	2.5	1	þ	20459060	

Building: 560 W. Mitchell St MOB	5th floor, Staff Elevator	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Components	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
Milwaukee		65	35		þ	18121703	
Location	
5th Staff Elevator Closet	

Building: 560 W. Mitchell St MOB	Basement, Area	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy		5th Above Ceiling Gastro Nurse Station	4"			þ	65661853	
Description	
Isolation	

Building: 560 W. Mitchell St MOB	Building-, Building-	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Devices	
Piping	
Location	Type	Size	Internal Date	
Basement Internal Piping	Steel		09/04/2018	
Hangers	Braces	Fittings	Identified	Antifreeze	ScanID	
Normal	Normal				49892353	

Building: 560 W. Mitchell St MOB	Penthouse	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	Potter Electric	VSR-F	30 secs	2.5	1-35	þ	20459080	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Alenco	BFV	Penthouse	4"			þ	36606926	
Description	
Isolation	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Milwaukee	BB-SC80	Penthouse	2"			þ	20459065	
Description	
Isolation	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
United Brass		95	21 sec		þ	36606530	
Location	
Penthouse	
Devices	
Gauge	
Location	Service Date	
Penthouse	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Ashcroft	SG3	50	Water	1/4	þ	36606925	
Gauge	
Location	Service Date	
Penthouse Top of penthouse stairs	03/31/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Argco	SG3	90	Water	1/4	þ	18121704	

Building: 560 W. Mitchell St MOB	Staircase A	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Standpipe	
	Wet System	Dry System		
Location	Type	Flow Test GPM	Flow Test PSI	Hydro PSI	ScanID	
Basement - 6 East Stairwell A	Class II	345	110 - 55		71337575	

Building: 560 W. Mitchell St MOB	Staircase B	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Standpipe	
	Wet System	Dry System		
Location	Type	Flow Test GPM	Flow Test PSI	Hydro PSI	ScanID	
Basement - 5 East Stairwell B	Class II	251	110 - 55		71337576	

Building: 560 W. Mitchell St MOB	Staircase C	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Standpipe	
	Wet System	Dry System		
Location	Type	Flow Test GPM	Flow Test PSI	Hydro PSI	ScanID	
Basement - E East Stairwell C	Class II	251	110 - 55		71337577	

Building: 560 W. Mitchell St MOB	main floor, Area- outside main riser roo	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor		30 sec	2.5	1	þ	20458236	
Devices	
Fire Dep't Connection	
Location	Type	BallDrip	Rotating Swivels	Size	OK	ScanID	
Basement Riser rm	Wall	Yes	Yes	4"	þ	38839441	
Sprinkler Box	
Qty	Tool Available?	SIN List?	Size	Manufacturer	Location	OK	ScanID	
12        	Yes	Yes	12 unit	American	Basement Riser room	þ	36606916	
6         	Yes	Yes	12 unit	American	Basement Riser room	þ	75205009	
Sprinkler Box Spares	
Qty	Type	Manufacturer	Location	OK	ScanID	
5         	Pendant	Viking	Basement Riser room	þ	75205008	
Temperature	KFactor	Size	Finish	Response Time	
155		1/2”	Chrome	Fast Response	
Sprinkler Box Spares	
Qty	Type	Manufacturer	Location	OK	ScanID	
4         	Upright	Viking	Basement Riser room	þ	75205007	
Temperature	KFactor	Size	Finish	Response Time	
155		1/2”	Brass	Standard Response	
Sprinkler Box Spares	
Qty	Type	Manufacturer	Location	OK	ScanID	
3         	Recessed Pendant	Victaulic	Basement Riser room	þ	75205006	
Temperature	KFactor	Size	Finish	Response Time	
155	5.6	1/2”	Chrome	Fast Response	

Building: 560 W. Mitchell St MOB	main floor, Area-staircase A	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor		39 sec	2.5	1-3 52	þ	20459115	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy		Basement Inside Hospital Storage	4"			þ	20458221	
Description	
Isolation	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Alenco	BFV	Basement Inside Stairwell A	2.5"			þ	20459116	
Description	
Isolation	

Building: 560 W. Mitchell St MOB	main floor, Area-staircase B	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Pressure Switch	
Type	Description	Manufacturer	Low	High	Zone/Address	OK	ScanID	
Low	Supervisory	System Sensor	60		1-03 28	þ	18121698	
Components	
Backflow Prevention	
Manufacturer	Model #	Size	Type	Service Type	Install Date	
Apollo	4D-200	8"	Double Check	Fire Line	03/31/2008	
ScanID	Water Purveyor	Location	Meter Account #	Serial Number	
47161127		Basement Riser rm tested 3/12/22 by other vendor		NE-U25	
Initial Test	
Check Valve 1	Check Valve 2	Relief Valve	Pressure Vacuum Breaker	
				
Held At	Repairs or Notes	
		
Final Test	
Check Valve 1	Check Valve 2	Relief Valve	Pressure Vacuum Breaker	
				
Held At	Condition of Control Valve 1	Condition of Control Valve 2	
			
Check Valve	
Type	Location	Internal Date	Size	OK	ScanID	
Flanged	Basement Riser 
room	09/12/2019	6"	þ	65660252	
Flanged	Basement Riser room	09/12/2019	8"	þ	36606914	
Flanged	Basement Inside Stairwell A	03/31/2019	2.5"	þ	47161122	
Flanged	1st Inside Stairwell B	03/31/2019	2.5"	þ	47161125	
Grooved	2nd Inside Stairwell C	03/31/2019	2.5"	þ	47161124	
Grooved	2nd Inside Stairwell B Riser 
room	09/11/2019	2.5"	þ	47161126	
Grooved	3rd Inside Stairwell B	09/11/2019	2.5"	þ	47161121	
Grooved	3rd Inside Stairwell C	03/31/2019	2.5"	þ	47161123	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	AWWA	Basement Riser room	8"			þ	20458237	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	D-1	Basement Riser room	8"			þ	36606527	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy		Basement Riser room	8"			þ	20458238	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	D-1	Basement Riser room	8"			þ	36606528	
Description	
Main Control	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
Elkhart		80	35 sec		þ	18121696	
Location	
Basement Closet Beside Stairwell A	
Devices	
Drain	
Current Inspection	
Type	Location	Size	Supply psi	Restored psi	Residual psi	Sec	OK	ScanID	
Main	Basement Riser 
room	2"	105	90	43	14 sec	þ	36606526	
Previous Inspections	
June 24, 2022	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	Basement Riser 
room	2"	95	90	70		þ	36606526	
March 22, 2022	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	Basement Riser 
room	2"	97	95	70		þ	36606526	
Gauge	
Location	Service Date	
Basement Closet beside Stairwell A	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Argco	SG3	110	Oil	1/4	þ	36606913	
Gauge	
Location	Service Date	
Basement Riser 
room	03/31/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Viking	SG3	130	Water	1/4	þ	47161128	
Gauge	
Location	Service Date	
Basement Riser 
room	09/04/2018	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Argco	SG3	100	Water	1/4	þ	18121697	

Building: 560 W. Mitchell St MOB	main floor, Area-staircase C	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Tyco	BFV-300	Basement Above Ceiling Stairwell C	4"			þ	75205000	
Description	
Isolation	

Building: 560 W. Mitchell St MOB	main floor, Area-staircase c	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy		Basement Above Ceiling Stairwell A	4"			þ	36606525	
Description	
Isolation	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Milwaukee	BB-SOSO	5th Above Ceiling Stairwell C	4"			þ	20459059	
Description	
Isolation	

Inventory & Warranty Report	
Generated by: BuildingReports.com	
Building: 560 W. Mitchell St MOB	
The Inventory & Warranty Report lists each of the devices and items that are included in your Inspection Report. A complete inventory count by device type and category is provided. Items installed within the last 90 days, within the last year, and devices installed for two years or more are grouped together for easy reference.	

Device or Type	Category	% of Inventory	Quantity	
Backflow Prevention	Valve	1.39%	1	
Check Valve	Valve	11.11%	8	
Control Valve	Valve	27.78%	20	
Drain	Device	1.39%	1	
Fire Dep't Connection	Hose	1.39%	1	
Gauge	Device	16.67%	12	
Inspector's Test	Valve	9.72%	7	
Piping	Sprinkler	1.39%	1	
Pressure Switch	Alarm	1.39%	1	
Sprinkler Box	Sprinkler	2.78%	2	
Sprinkler Box Spares	Sprinkler	4.17%	3	
Standpipe	Hose	4.17%	3	
Waterflow Switch	Alarm	16.67%	12	

Device Type	Qty	Model #	Type	Description	Install Date	
In Service - 1 Year to 2 Years	
main floor Wet Pipe, Area-staircase C	
Control Valve	1	BFV-300	Butterfly	Isolation	02/26/2021	
In Service - 2 Years to 3 Years	
main floor Wet Pipe, Area-staircase B	
Gauge	1	SG3	Supply Pressure		03/31/2020	
In Service - 3 Years to 5 Years	
1st floor Wet Pipe, Area-staircase c	
Gauge	1	SG3	System Pressure		09/04/2018	
2nd floor Wet Pipe, Area-staircase B	
Gauge	1	SG3	System Pressure		09/04/2018	
3rd floor Wet Pipe, Area-staircase c	
Gauge	1	SG3	System Pressure		09/04/2018	
4th floor Wet Pipe, Area-staircase B	
Gauge	1	SG3	System Pressure		09/04/2018	
5th floor Wet Pipe, Area-staircase B	
Gauge	1	SG3	System Pressure		09/04/2018	
Gauge	2	SG3	System Pressure		09/04/2018	
Building- Wet Pipe, Building-	
Piping	1		Steel		09/04/2018	
Penthouse Wet Pipe	
Gauge	1	SG3	System Pressure		09/04/2018	
main floor Wet Pipe, Area-staircase B	
Gauge	2	SG3	System Pressure		09/04/2018	
Penthouse Wet Pipe	
Gauge	1	SG3	System Pressure		03/31/2018	
In Service - 5 Years to 10 Years	
1st floor Wet Pipe, Area-staircase B	
Control Valve	1		Butterfly	Isolation	03/31/2017	
1st floor Wet Pipe, Area-staircase b	
Waterflow Switch	1	VSR-D	Vane	Alarm	03/31/2017	
1st floor Wet Pipe, Area-staircase c	
Inspector's Test	1	1000			03/31/2017	
2nd floor Wet Pipe, Area-staircase B	
Control Valve	1		Ball	Isolation	03/31/2017	
Inspector's Test	1	52S1			03/31/2017	
Waterflow Switch	1	VSR-F	Vane	Alarm	03/31/2017	
2nd floor Wet Pipe, Area-staircase C	
Control Valve	1	BFV	Butterfly	Isolation	03/31/2017	
Waterflow Switch	1	VSR-F	Vane	Alarm	03/31/2017	
3rd floor Wet Pipe, Area-staircase B	
Control Valve	1		Ball	Isolation	03/31/2017	
Waterflow Switch	2	WFD-25	Vane	Alarm	03/31/2017	
3rd floor Wet Pipe, Area-staircase c	
Control Valve	1		Butterfly	Isolation	03/31/2017	
Inspector's Test	1	52S1			03/31/2017	
4th floor Wet Pipe, Area-staircase B	
Inspector's Test	1	1000			03/31/2017	
Control Valve	1	BB-SCS	Butterfly	Isolation	03/31/2017	
Waterflow Switch	1		Vane	Alarm	03/31/2017	
4th floor Wet Pipe, Area-staircase C	
Control Valve	1	BB-SOSO	Ball	Isolation	03/31/2017	
Waterflow Switch	1	WFD-25	Vane	Alarm	03/31/2017	
5th floor Wet Pipe, Area-staircase B	
Control Valve	1		Ball	Isolation	03/31/2017	
Waterflow Switch	1		Vane	Alarm	03/31/2017	
5th floor Wet Pipe, Area-staircase C	
Waterflow Switch	1	WFD-25	Vane	Alarm	03/31/2017	
5th floor Wet Pipe, Staff Elevator	
Inspector's Test	1				03/31/2017	
Basement Wet Pipe, Area	
Control Valve	1		OS&Y	Isolation	03/31/2017	
Penthouse Wet Pipe	
Control Valve	1	BFV	Butterfly	Isolation	03/31/2017	
Control Valve	1	BB-SC80	Butterfly	Isolation	03/31/2017	
Waterflow Switch	1	VSR-F	Vane	Alarm	03/31/2017	
Inspector's Test	1				03/31/2017	
main floor Wet Pipe, Area- outside main riser roo	
Fire Dep't Connection	1		Wall		03/31/2017	
Sprinkler Box	2				03/31/2017	
Waterflow Switch	1		Vane	Alarm	03/31/2017	
Sprinkler Box Spares	1	lV2708	Recessed Pendant		03/31/2017	
Sprinkler Box Spares	1	M	Pendant		03/31/2017	
Sprinkler Box Spares	1	M	Upright		03/31/2017	
main floor Wet Pipe, Area-staircase A	
Control Valve	1	BFV	Butterfly	Isolation	03/31/2017	
Control Valve	1		OS&Y	Isolation	03/31/2017	
Waterflow Switch	1		Vane	Alarm	03/31/2017	
main floor Wet Pipe, Area-staircase B	
Drain	1		Main		03/31/2017	
Inspector's Test	1				03/31/2017	
Check Valve	1		Flanged		03/31/2017	
Check Valve	1	A-2	Flanged		03/31/2017	
Control Valve	1		OS&Y	Main Control	03/31/2017	
Control Valve	1	AWWA	OS&Y	Main Control	03/31/2017	
Control Valve	2	D-1	OS&Y	Main Control	03/31/2017	
main floor Wet Pipe, Area-staircase c	
Control Valve	1		OS&Y	Isolation	03/31/2017	
Control Valve	1	BB-SOSO	OS&Y	Isolation	03/31/2017	
Wet Pipe, Staircase A	
Standpipe	1		Class II		03/31/2015	
Wet Pipe, Staircase B	
Standpipe	1		Class II		03/31/2015	
Wet Pipe, Staircase C	
Standpipe	1		Class II		03/31/2015	
main floor Wet Pipe, Area-staircase B	
Pressure Switch	1	EPS40-2	Low	Supervisory	03/31/2015	
In Service - 10 Years to 15 Years	
main floor Wet Pipe, Area-staircase B	
Backflow Prevention	1	4D-200	Double Check		03/31/2008	
In Service - 25 Years or Older	
main floor Wet Pipe, Area-staircase B	
Check Valve	2		Flanged		03/31/1996	
Check Valve	2		Grooved		03/31/1996	
Check Valve	2	90	Grooved		03/31/1996	

Zone Address Report
Generated by: BuildingReports.com

Building: 560 W. Mitchell St MOB	
The Zone Address Report lists all of the devices and items that have an individual address, or are grouped together under a common zone.  The device type, location and description are included for your reference. For more information on the device, use the link provided under ScanID.	
Address	Device Type	Location	Type	ScanID	
Control Panel 1	
Zone/Address: 03	
28	Pressure Switch	Basement Riser room	Low	18121698	
Zone/Address: 3	
41	Control Valve	Basement Riser room	OS&Y	20458237	
42	Control Valve	Basement Above Ceiling Stairwell A	OS&Y	36606525	
49	Control Valve	Basement Riser room	OS&Y	20458238	
52	Waterflow Switch	Basement Inside Stairwell A	Vane	20459115	
53	Control Valve	Basement Inside Stairwell A	Butterfly	20459116	
35	Waterflow Switch	Penthouse	Vane	20459080	
36	Control Valve	Penthouse	Butterfly	36606926	
37	Control Valve	Penthouse	Butterfly	20459065