Fire Alarm and Life Safety System Inspection Certificate
For
	Wheaton Office		
	120 East Liberty Drive		
	Wheaton, IL 60187		
Tested to NFPA 72 Standards
This Inspection was performed in accordance with applicable NFPA Standards.  The subsequent pages of this report provide performance measurements, listed ranges of acceptable results, and complete documentation of the inspection.  Whenever discrepancies exist between acceptable performance standards and actual test results, notes and/or recommended solutions have been proposed or provided for immediate review and approval.

Inspection Date
Dec 21, 2022
Building: Wheaton Office	Company: SMG & CAS Security Holdings LLC	
Contact: Nathan Sands	Contact: Bill White	
Title: Property Manager	Title: Inspector	

Executive Summary
Generated by: BuildingReports.com

Building Information	
  Building: Wheaton Office	Contact: Nathan Sands	
  Address: 120 East Liberty Drive	Phone: 630-230-1221	
  Address: 	Fax: 	
  City/State/ZIP Code: Wheaton, IL 60187	Mobile: 	
  Country: United States of America	Email: nsands@wavelandprop.com	
Inspection Performed By	
  Company: SMG & CAS Security Holdings LLC	Inspector: Bill White	
  Address: 120 King Street	Phone: 630-417-0231	
  Address: 	Fax: 	
  City/State/ZIP Code: Elk Grove Village, Illinois 60007-1111	Mobile: 	
  Country: United States of America	Email: bill.white@smgsecurity.com	
System Control Unit	
  Manufacturer: Silent Knight	Inspection Date: 12/21/2022	IDC Style: 	
  Model Number: IFP-1000	Install Date: 09/18/2014	SLC Style: 	
  Software Version: 	Version Date: 09/18/2014	NAC Style: Y	
  Location: Pump Room	Current Protection: Breaker	

Monitoring	
  Company: DuCom	Phone: 6306908245	Account #: 6339	

Inspection Summary	
Category	Total Items	Serviced	Passed	Failed/Other	
	Qty	%	Qty	%	Qty	%	Qty	%	
  Control	25	18.94%	25	100.00%	25	100.00%	0	0.00%	
  Indicating	1	0.76%	1	100.00%	1	100.00%	0	0.00%	
  Initiating	83	62.88%	83	100.00%	83	100.00%	0	0.00%	
  Supervisory	23	17.42%	23	100.00%	23	100.00%	0	0.00%	
Totals	132	100%	132	100.00%	132	100.00%	0	0.00%	

Certification	
Company: SMG & CAS Security Holdings LLC	Building: Wheaton Office	
Inspector: Bill White	Contact: Nathan Sands	
		
Signed: Dec 21, 2022	Signed: Dec 21, 2022	

Inspection & Testing
Generated by: BuildingReports.com

Building: Wheaton Office	Control Panel: 1 - Silent Knight IFP-1000  	
The Inspection & Testing section lists all of the items inspected in your building.  Items are grouped by Passed or Failed/Other. Items are listed by Category. Each item includes the services performed, and the time & date at which testing occurred.	

Device Type	Location	Service	Time	Date	
Passed	
Control	
Annunciator	North Main Entrance	Tested	6:36:26 AM	12/21/2022	
Battery	2nd MPOP Room	Tested	7:20:46 AM	12/21/2022	
Battery	2nd MPOP Room	Tested	7:21:07 AM	12/21/2022	
Battery	4th MPOP Room	Tested	6:59:13 AM	12/21/2022	
Battery	4th MPOP Room	Tested	6:59:28 AM	12/21/2022	
Battery	4th MPOP Room	Tested	6:59:51 AM	12/21/2022	
Battery	4th MPOP Room	Tested	7:00:35 AM	12/21/2022	
Battery	4th MPOP Room	Tested	7:00:53 AM	12/21/2022	
Battery	4th MPOP Room	Tested	7:01:07 AM	12/21/2022	
Battery	4th MPOP Room	Tested	7:02:11 AM	12/21/2022	
Battery	4th MPOP Room	Tested	7:02:30 AM	12/21/2022	
Battery	FACP Pump Room	Tested	7:31:19 AM	12/21/2022	
Battery	FACP Pump Room	Tested	7:31:25 AM	12/21/2022	
Battery	FCPS Pump Room	Tested	8:44:38 AM	12/21/2022	
Battery	FCPS Pump Room	Tested	8:44:54 AM	12/21/2022	
Battery	Suite 190 FCPS	Tested	8:20:59 AM	12/21/2022	
Battery	Suite 190 FCPS Room	Tested	8:21:14 AM	12/21/2022	
Control Panel	Pump Room	Tested	7:27:53 AM	12/21/2022	
Power Supply	2nd MPOP Room	Tested	7:19:15 AM	12/21/2022	
Power Supply	4th MPOP Room	Tested	6:58:52 AM	12/21/2022	
Power Supply	4th MPOP Room	Tested	7:02:55 AM	12/21/2022	
Power Supply	4th MPOP Room	Tested	7:02:59 AM	12/21/2022	
Power Supply	4th MPOP Room	Tested	7:03:03 AM	12/21/2022	
Power Supply	Pump Room	Tested	8:37:40 AM	12/21/2022	
Power Supply	Suite 190 Kitchen	Tested	8:20:36 AM	12/21/2022	
Indicating	
Horn/Strobe	Horns Strobes Test Good 12-21-2022	Tested	7:43:16 AM	12/21/2022	
Initiating	
Duct Detector	2nd East Office Activ IT Closet	Tested	6:20:27 AM	12/21/2022	
Duct Detector	2nd West Office Electrical closet	Tested	6:19:19 AM	12/21/2022	
Duct Detector	3rd East Office Hallway	Tested	6:17:40 AM	12/21/2022	
Duct Detector	3rd West Office	Tested	6:16:22 AM	12/21/2022	
Duct Detector	4th East Office South	Tested	6:12:37 AM	12/21/2022	
Duct Detector	4th West Office	Tested	6:11:12 AM	12/21/2022	
Duct Detector	5th North IT Lab	Tested	6:08:51 AM	12/21/2022	
Duct Detector	5th West Office	Tested	6:09:45 AM	12/21/2022	
Duct Detector	Suite 190 Sushi Beverage Area	Tested	6:26:18 AM	12/21/2022	
Duct Detector	Suite 190 Sushi Beverage Area	Tested	6:26:23 AM	12/21/2022	
Duct Detector	Suite 190 Sushi Kitchen	Tested	6:25:32 AM	12/21/2022	
Heat Detector	1st Electrical Room	Tested	8:25:14 AM	12/21/2022	
Heat Detector	1st MPOP Room	Tested	8:34:16 AM	12/21/2022	
Heat Detector	1st Main Electrical Room	Tested	8:25:22 AM	12/21/2022	
Heat Detector	1st Main Electrical Room	Tested	8:25:25 AM	12/21/2022	
Heat Detector	2nd Electrical Room	Tested	7:17:04 AM	12/21/2022	
Heat Detector	2nd MPOP Room	Tested	7:16:59 AM	12/21/2022	
Heat Detector	3rd Electrical Room	Tested	7:10:25 AM	12/21/2022	
Heat Detector	3rd MPOP Room	Tested	7:13:07 AM	12/21/2022	
Heat Detector	4th Electrical Room	Tested	7:06:25 AM	12/21/2022	
Heat Detector	4th MPOP Room	Tested	7:02:44 AM	12/21/2022	
Heat Detector	5th Electrical Room	Tested	6:50:05 AM	12/21/2022	
Heat Detector	5th Elevator Room	Tested	6:49:52 AM	12/21/2022	
Heat Detector	5th Elevator Room	Tested	6:54:40 AM	12/21/2022	
Heat Detector	5th MPOP Room	Tested	6:52:28 AM	12/21/2022	
Heat Detector	5th Shaft	Tested	6:49:15 AM	12/21/2022	
Heat Detector	Garage Electrical Room	Tested	8:10:49 AM	12/21/2022	
Heat Detector	LL Pit	Tested	8:09:22 AM	12/21/2022	
Heat Detector	LL Pit	Tested	8:09:26 AM	12/21/2022	
Heat Detector	LL Pit	Tested	8:09:39 AM	12/21/2022	
Pull Station	1st Center Lobby	Tested	8:24:16 AM	12/21/2022	
Pull Station	1st East Lobby	Tested	6:29:52 AM	12/21/2022	
Pull Station	1st North Vestibule	Tested	6:37:36 AM	12/21/2022	
Pull Station	1st South Vestibule	Tested	6:38:13 AM	12/21/2022	
Pull Station	2nd East Stairs	Tested	7:22:41 AM	12/21/2022	
Pull Station	2nd West Stairs	Tested	7:35:58 AM	12/21/2022	
Pull Station	3rd East Stairs	Tested	7:14:17 AM	12/21/2022	
Pull Station	3rd West Stairs	Tested	7:13:39 AM	12/21/2022	
Pull Station	4th West Stairs	Tested	6:58:22 AM	12/21/2022	
Pull Station	5th East Stairs	Tested	6:55:30 AM	12/21/2022	
Pull Station	5th West Stairs	Tested	6:54:20 AM	12/21/2022	
Pull Station	Pump Room	Tested	8:08:05 AM	12/21/2022	
Pull Station	LL East Stairs	Tested	8:09:58 AM	12/21/2022	
Pull Station	LL West Stairs	Tested	8:11:28 AM	12/21/2022	
Pull Station	Suite 100 North Exit	Tested	6:31:39 AM	12/21/2022	
Pull Station	Suite 140 Main Entrance	Tested	6:30:43 AM	12/21/2022	
Pull Station	Suite 190 North Exit	Tested	8:15:29 AM	12/21/2022	
Pull Station	Suite 190 North Main Entrance	Tested	8:16:03 AM	12/21/2022	
Pull Station	Suite 190 West Dining Room Exit	Tested	8:16:52 AM	12/21/2022	
Pull Station	Suite 190 West Kitchen Exit	Tested	8:19:57 AM	12/21/2022	
Smoke Detector	1st Electrical Room	Tested/Cleaned	8:25:11 AM	12/21/2022	
Smoke Detector	1st Elevator Lobby	Tested/Cleaned	8:29:31 AM	12/21/2022	
Smoke Detector	1st MPOP Room	Tested/Cleaned	8:34:12 AM	12/21/2022	
Smoke Detector	1st Main Electrical Room	Tested/Cleaned	8:25:18 AM	12/21/2022	
Smoke Detector	1st Main Electrical Room	Tested/Cleaned	8:25:30 AM	12/21/2022	
Smoke Detector	1st Maintenance Elevator Lobby	Tested/Cleaned	8:25:36 AM	12/21/2022	
Smoke Detector	2nd Electrical Room	Tested/Cleaned	7:17:50 AM	12/21/2022	
Smoke Detector	2nd Elevator Lobby	Tested/Cleaned	7:18:36 AM	12/21/2022	
Smoke Detector	2nd MPOP Room	Tested/Cleaned	7:20:53 AM	12/21/2022	
Smoke Detector	3rd Electrical Room	Tested/Cleaned	7:10:17 AM	12/21/2022	
Smoke Detector	3rd Elevator Lobby	Tested/Cleaned	7:10:21 AM	12/21/2022	
Smoke Detector	3rd MPOP Room	Tested/Cleaned	7:13:12 AM	12/21/2022	
Smoke Detector	4th Electrical Room	Tested/Cleaned	7:06:31 AM	12/21/2022	
Smoke Detector	4th Elevator Lobby	Tested/Cleaned	7:06:35 AM	12/21/2022	
Smoke Detector	4th MPOP Room	Tested/Cleaned	7:03:38 AM	12/21/2022	
Smoke Detector	5th Electrical Room	Tested/Cleaned	6:54:27 AM	12/21/2022	
Smoke Detector	5th Elevator Lobby	Tested/Cleaned	6:50:11 AM	12/21/2022	
Smoke Detector	5th Elevator Room	Tested/Cleaned	6:49:58 AM	12/21/2022	
Smoke Detector	5th Elevator Room	Tested/Cleaned	6:54:44 AM	12/21/2022	
Smoke Detector	5th MPOP Room	Tested/Cleaned	6:52:25 AM	12/21/2022	
Smoke Detector	5th Shaft	Tested/Cleaned	6:48:18 AM	12/21/2022	
Smoke Detector	5th Shaft	Tested/Cleaned	6:48:22 AM	12/21/2022	
Smoke Detector	Garage Electrical Room	Tested/Cleaned	7:35:24 AM	12/21/2022	
Smoke Detector	Garage Elevator Lobby	Tested/Cleaned	8:08:11 AM	12/21/2022	
Smoke Detector	LL Pit	Tested/Cleaned	6:48:25 AM	12/21/2022	
Smoke Detector	LL Pit	Tested/Cleaned	6:48:30 AM	12/21/2022	
Waterflow Switch	2nd East Stairs	Tested	7:15:13 AM	12/21/2022	
Waterflow Switch	3rd East Stairs	Tested	7:14:41 AM	12/21/2022	
Waterflow Switch	4th East Stairs	Tested	6:56:35 AM	12/21/2022	
Waterflow Switch	5th East Stairs	Tested	6:55:54 AM	12/21/2022	
Waterflow Switch	Pump Room	Tested	8:01:21 AM	12/21/2022	
Waterflow Switch	Pump Room	Tested	8:01:27 AM	12/21/2022	
Waterflow Switch	LL East Stairs	Tested	8:09:43 AM	12/21/2022	
Supervisory	
Fire Pump Power	Pump Room	Tested	8:01:43 AM	12/21/2022	
Fire Pump Trouble	4th East Stairs	Tested	6:57:10 AM	12/21/2022	
Tamper Switch	1st West Stairs	Tested	7:24:15 AM	12/21/2022	
Tamper Switch	2nd East Stairs	Tested	7:15:19 AM	12/21/2022	
Tamper Switch	3rd East Stairs	Tested	7:14:46 AM	12/21/2022	
Tamper Switch	4th East Stairs	Tested	6:56:40 AM	12/21/2022	
Tamper Switch	5th East Stairs	Tested	6:55:58 AM	12/21/2022	
Tamper Switch	Garage Elevator	Tested	8:07:55 AM	12/21/2022	
Tamper Switch	Garage Elevator	Tested	8:13:09 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	7:59:49 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:00:02 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:00:10 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:00:41 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:00:46 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:02:06 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:02:15 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:02:19 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:02:38 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:02:43 AM	12/21/2022	
Tamper Switch	Pump Room	Tested	8:02:58 AM	12/21/2022	
Tamper Switch	Pump Room CLOSED	Tested	8:02:26 AM	12/21/2022	
Tamper Switch	Maintenance Garage Elevator Sticker On Outlet	Tested	8:13:19 AM	12/21/2022	
Tamper Switch	LL East Stairs	Tested	8:09:47 AM	12/21/2022	

Service Summary	
Generated by: BuildingReports.com	
Building: Wheaton Office	
The Service Summary section provides an overview of the services performed in this report.	

Device Type	Service	Quantity	
Passed	
Annunciator	Tested	1	
Battery	Tested	16	
Control Panel	Tested	1	
Duct Detector	Tested	11	
Fire Pump Power	Tested	1	
Fire Pump Trouble	Tested	1	
Heat Detector	Tested	19	
Horn/Strobe	Tested	1	
Power Supply	Tested	7	
Pull Station	Tested	20	
Smoke Detector	Tested/Cleaned	26	
Tamper Switch	Tested	21	
Waterflow Switch	Tested	7	
Total	132	
Grand Total	132	

Inventory & Warranty Report	
Generated by: BuildingReports.com	
Building: Wheaton Office	Control Panel: 1 - Silent Knight IFP-1000	
The Inventory & Warranty Report lists each of the devices and items that are included in your Inspection Report. A complete inventory count by device type and category is provided. Items installed within the last 90 days, within the last year, and devices installed for two years or more are grouped together for easy reference.	

Device or Type	Category	% of Inventory	Quantity	
Annunciator	Control	0.76%	1	
Battery	Control	12.12%	16	
Control Panel	Control	0.76%	1	
Duct Detector	Initiating	8.33%	11	
Fire Pump Power	Supervisory	0.76%	1	
Fire Pump Trouble	Supervisory	0.76%	1	
Heat Detector	Initiating	14.39%	19	
Horn/Strobe	Indicating	0.76%	1	
Power Supply	Control	5.30%	7	
Pull Station	Initiating	15.15%	20	
Smoke Detector	Initiating	19.70%	26	
Tamper Switch	Supervisory	15.91%	21	
Waterflow Switch	Initiating	5.30%	7	

Type	Qty	Model #	Description	Install Date	
New (under 90 days)	
Horn/Strobe	1			12/21/2022	
In Service - 90 Days - 1 Year	
DuraCell	
Battery	2	Dura12-18NB	Sealed Lead Acid	06/21/2022	
Battery	2	Dura12-8F	Sealed Lead Acid	06/21/2022	
Duracell	
Battery	2	Dura12-8F	Sealed Lead Acid	06/21/2022	
Power Patrol	
Battery	9	SLA1075	Sealed Lead Acid	06/21/2022	
In Service - 5 Years to 10 Years	
AES	
Smoke Detector	1	SD505-APS	Photoelectric	09/18/2014	
Fire Lite	
Pull Station	1	BG-12LX	Dual Action	09/18/2014	
Master	
Fire Pump Power	1	MCA-50-46-HX		09/18/2014	
Milwaukee	
Tamper Switch	2	BSB-SCSO		09/18/2014	
Potter Electric	
Tamper Switch	3	OSYSU-2		09/18/2014	
Waterflow Switch	2	VSR-F		09/18/2014	
Power Patrol	
Battery	1	SLA1075	Sealed Lead Acid	09/18/2014	
Silent Knight	
Control Panel	1	IFP-1000		09/18/2014	
Fire Pump Trouble	1	PS-DA		09/18/2014	
Heat Detector	17	SD505-HT		09/18/2014	
Heat Detector	2	SD505-HT	Fixed Temperature	09/18/2014	
Power Supply	7	5499		09/18/2014	
Pull Station	19	PS-DA	Dual Action	09/18/2014	
Smoke Detector	25	SD505-APS	Photoelectric	09/18/2014	
System Sensor	
Duct Detector	7	RTS451	Photoelectric	09/18/2014	
Duct Detector	4	RTS451KEY	Photoelectric	09/18/2014	
Waterflow Switch	5	WFD25		09/18/2014	
Victaulic	
Tamper Switch	1	705		09/18/2014	
Tamper Switch	13	705W		09/18/2014	
Tamper Switch	2	728		09/18/2014	
Silent Knight	
Annunciator	1	RA-100	LED List	04/18/2014	

Zone Address Report
Generated by: BuildingReports.com

Building: Wheaton Office	Control Panel: 1 - Silent Knight  IFP-1000	
The Zone Address Report lists all of the devices and items that have an individual address, or are grouped together under a common zone.  The device type, location, and description are included for your reference.	
Address	Device Type	Location	Type	ScanID	
Zone/Circuit: M	
01	Waterflow Switch	Pump Room		30565189	
01	Pull Station	Suite 100 North Exit	Dual Action	39732916	
02	Waterflow Switch	Pump Room		57331475	
02	Pull Station	Suite 140 Main Entrance	Dual Action	39732917	
03	Fire Pump Power	Pump Room		32703771	
03	Tamper Switch	Pump Room		30565184	
03	Tamper Switch	Pump Room		30565185	
03	Tamper Switch	Pump Room		30565186	
04	Tamper Switch	Pump Room		30565172	
04	Tamper Switch	Pump Room		30565173	
05	Tamper Switch	Pump Room		30565176	
05	Tamper Switch	Pump Room		30565178	
05	Tamper Switch	Pump Room		30565179	
05	Tamper Switch	Pump Room		30565180	
05	Tamper Switch	Pump Room		30565182	
05	Tamper Switch	Pump Room		30565183	
05	Tamper Switch	Pump Room CLOSED		30565181	
06	Pull Station	1st East Lobby	Dual Action	32703913	
09	Pull Station	Pump Room	Dual Action	32703915	
10	Smoke Detector	1st Main Electrical Room	Photoelectric	32703997	
11	Heat Detector	1st Main Electrical Room		32703998	
12	Pull Station	1st South Vestibule	Dual Action	32703914	
13	Pull Station	1st Center Lobby	Dual Action	32703912	
14	Heat Detector	1st Main Electrical Room		32703999	
15	Smoke Detector	1st Main Electrical Room	Photoelectric	32704000	
16	Smoke Detector	1st Maintenance Elevator Lobby	Photoelectric	32704001	
17	Smoke Detector	1st Electrical Room	Photoelectric	32704003	
18	Heat Detector	1st Electrical Room		32704002	
19	Smoke Detector	1st Elevator Lobby	Photoelectric	32703986	
22	Smoke Detector	1st MPOP Room	Photoelectric	32703996	
23	Heat Detector	1st MPOP Room		32703995	
24	Heat Detector	Garage Electrical Room	Fixed Temperature	32703970	
25	Smoke Detector	Garage Electrical Room	Photoelectric	32703969	
26	Heat Detector	LL Pit		32703779	
27	Smoke Detector	LL Pit	Photoelectric	32703783	
28	Smoke Detector	Garage Elevator Lobby	Photoelectric	32703971	
31	Smoke Detector	LL Pit	Photoelectric	32703782	
32	Heat Detector	LL Pit		32703778	
34	Heat Detector	LL Pit		32703777	
35	Pull Station	LL West Stairs	Dual Action	32703911	
36	Pull Station	LL East Stairs	Dual Action	32703910	
37	Pull Station	2nd East Stairs	Dual Action	32703909	
39	Duct Detector	2nd East Office Activ IT Closet	Photoelectric	32703897	
40	Smoke Detector	2nd Electrical Room	Photoelectric	32703974	
41	Heat Detector	2nd Electrical Room		32703973	
42	Smoke Detector	2nd Elevator Lobby	Photoelectric	32703975	
45	Heat Detector	2nd MPOP Room		32703972	
46	Smoke Detector	2nd MPOP Room	Photoelectric	32703994	
47	Pull Station	2nd West Stairs	Dual Action	32703908	
49	Duct Detector	2nd West Office Electrical closet	Photoelectric	32703895	
50	Pull Station	3rd East Stairs	Dual Action	32703905	
51	Tamper Switch	1st West Stairs		32703775	
51	Tamper Switch	Maintenance Garage Elevator Sticker On Outlet		32703774	
52	Duct Detector	3rd East Office Hallway	Photoelectric	32703894	
53	Heat Detector	3rd Electrical Room		32703988	
54	Smoke Detector	3rd Electrical Room	Photoelectric	32703989	
55	Smoke Detector	3rd Elevator Lobby	Photoelectric	32703990	
56	Pull Station	Suite 190 West Dining Room Exit	Dual Action	39732920	
57	Pull Station	Suite 190 West Kitchen Exit	Dual Action	76318903	
58	Heat Detector	3rd MPOP Room		32703987	
59	Smoke Detector	3rd MPOP Room	Photoelectric	32703984	
60	Pull Station	3rd West Stairs	Dual Action	32703904	
61	Pull Station	1st North Vestibule	Dual Action	32703903	
62	Duct Detector	3rd West Office	Photoelectric	32703893	
63	Fire Pump Trouble	4th East Stairs		32703902	
65	Duct Detector	4th East Office South	Photoelectric	32703892	
66	Heat Detector	4th Electrical Room		32703981	
67	Smoke Detector	4th Electrical Room	Photoelectric	32703982	
68	Smoke Detector	4th Elevator Lobby	Photoelectric	32703983	
70	Duct Detector	Suite 190 Sushi Beverage Area	Photoelectric	32703966	
71	Heat Detector	4th MPOP Room		32703976	
72	Smoke Detector	4th MPOP Room	Photoelectric	32703977	
73	Pull Station	4th West Stairs	Dual Action	32703901	
75	Duct Detector	4th West Office	Photoelectric	32703891	
76	Pull Station	5th East Stairs	Dual Action	32703900	
78	Duct Detector	5th North IT Lab	Photoelectric	32703890	
80	Heat Detector	5th Electrical Room		32703856	
81	Smoke Detector	5th Electrical Room	Photoelectric	32703857	
82	Heat Detector	5th Shaft		32703776	
83	Smoke Detector	5th Shaft	Photoelectric	32703781	
84	Heat Detector	5th Elevator Room		32703855	
85	Smoke Detector	5th Elevator Room	Photoelectric	32703854	
86	Smoke Detector	5th Elevator Lobby	Photoelectric	32703858	
87	Duct Detector	Suite 190 Sushi Beverage Area	Photoelectric	32703968	
88	Duct Detector	Suite 190 Sushi Kitchen	Photoelectric	32703967	
90	Smoke Detector	5th Shaft	Photoelectric	32703780	
92	Pull Station	Suite 190 North Main Entrance	Dual Action	39732919	
93	Heat Detector	5th Elevator Room		32703852	
94	Smoke Detector	5th Elevator Room	Photoelectric	32703853	
95	Heat Detector	5th MPOP Room	Fixed Temperature	32703873	
96	Smoke Detector	5th MPOP Room	Photoelectric	32703872	
97	Pull Station	5th West Stairs	Dual Action	32703899	
98	Pull Station	Suite 190 North Exit	Dual Action	39732918	
99	Duct Detector	5th West Office	Photoelectric	32703889	
103	Waterflow Switch	2nd East Stairs		32703866	
104	Tamper Switch	2nd East Stairs		32703865	
105	Waterflow Switch	3rd East Stairs		32703863	
106	Tamper Switch	3rd East Stairs		32703864	
107	Waterflow Switch	4th East Stairs		32703862	
108	Tamper Switch	4th East Stairs		32703861	
109	Waterflow Switch	5th East Stairs		32703860	
110	Tamper Switch	5th East Stairs		32703859	
123	Tamper Switch	Garage Elevator		32703772	
124	Tamper Switch	Garage Elevator		32703773	
125	Waterflow Switch	LL East Stairs		32703867	
126	Tamper Switch	LL East Stairs		32703868