Fire Alarm and Life Safety System Inspection Certificate
For
	560 W. Mitchell St MOB		
	560 W. Mitchell Street		
	Suite 202		
	Petoskey, MI 49770		
Tested to NFPA 72 Standards
This Inspection was performed in accordance with applicable NFPA Standards.  The subsequent pages of this report provide performance measurements, listed ranges of acceptable results, and complete documentation of the inspection.  Whenever discrepancies exist between acceptable performance standards and actual test results, notes and/or recommended solutions have been proposed or provided for immediate review and approval.
Annual Inspection
Inspection Date
Dec 22, 2022
Building: 560 W. Mitchell St MOB	Company: Vanguard Fire & Security Systems, Inc.	
Contact: Brian Lepird	Contact: Brandon Crain	
Title: Site Contact	Title: Technician	

Executive Summary
Generated by: BuildingReports.com

Building Information	
  Building: 560 W. Mitchell St MOB	Contact: Brian Lepird	
  Address: 560 W. Mitchell Street	Phone: 231-330-3225	
  Address: Suite 202	Fax: 	
  City/State/ZIP Code: Petoskey, MI 49770	Mobile: 	
  Country: United States of America	Email: blepird@landmarkleadership.com	
Inspection Performed By	
  Company: Vanguard Fire & Security Systems, Inc.	Inspector: Brandon Crain	
  Address: 2101 Martindale SW	Phone: 616-245-8719	
  Address: 	Fax: 	
  City/State/ZIP Code: Grand Rapids, MI 49509	Mobile: 	
  Country: United States of America	Email: service@vanguard-fire.com	
System Control Unit	
  Manufacturer: Johnson Controls	Inspection Date: 11/21/2022	IDC Style: B	
  Model Number: 3030	Install Date: 09/28/2015	SLC Style: 2	
  Software Version: 	Version Date: 09/28/2015	NAC Style: Y	
  Location: Basement Inside Electrical	Current Protection: Fuse	

Central Station Signal Verification	
  Type: Cellular	Mfg: Teleguard	Model #: TG-7	
  Test Time/Date: 11/21/22 9:34:53 AM	Restore Time: 	Note: 	

Type of Signal	Signal Confirmation	Notes	
Type: Alarm	Confirmed Time: 40sec.	Note: 	
Type: Supervisory	Confirmed Time: 38sec.	Note: 	
Type: Trouble	Confirmed Time: 33sec.	Note: 	

Inspection Summary	
Category	Total Items	Serviced	Passed	Failed/Other	
	Qty	%	Qty	%	Qty	%	Qty	%	
  Auxiliary	6	0.63%	6	100.00%	6	100.00%	0	0.00%	
  Control	32	3.38%	32	100.00%	32	100.00%	0	0.00%	
  Indicating	738	77.85%	738	100.00%	738	100.00%	0	0.00%	
  Initiating	150	15.82%	150	100.00%	150	100.00%	0	0.00%	
  Monitor	3	0.32%	3	100.00%	3	100.00%	0	0.00%	
  Supervisory	19	2.00%	19	100.00%	19	100.00%	0	0.00%	
Totals	948	100%	948	100.00%	948	100.00%	0	0.00%	

Certification	
Company: Vanguard Fire & Security Systems, Inc.	Building: 560 W. Mitchell St MOB	
Inspector: Brandon Crain	Contact: Brian Lepird	
		
Signed: Dec 22, 2022	Signed: 	

Brandon Crain Certifications	
Certification Type	Number	
NICET Fire Alarm Systems Level II	116477	

Discrepancy Report
Generated by: BuildingReports.com

Building: 560 W. Mitchell St MOB	Control Panel: N/A	
The Discrepancy Report consolidates each discrepancy listed within the various Testing sections of your Inspection. Discrepancies are listed by Category, and grouped by device type. The description of the problem is provided and where appropriate, code references are listed for your convenience. Any item that was inspected that is subject to a recall or part of a manufacturer’s replacement/upgrade program is included.	
Device Type	 Manufacturer	 ModelNumber	 Date	Qty	
Items listed for Recall or Replacement/Upgrade	
Pull Station	Johnson Controls	BGX-101L	04/01/2013	51	
More Information: https://buildings.honeywell.com/content/dam/hbtbt/en/documents/downloads/HFS%20BG-10%20Series%20Letter%20April%202013.pdf	

Inspection & Testing
Generated by: BuildingReports.com

Building: 560 W. Mitchell St MOB	Control Panel: 1 - Johnson Controls 3030  	
The Inspection & Testing section lists all of the items inspected in your building.  Items are grouped by Passed or Failed/Other. Items are listed by Category. Each item includes the services performed, and the time & date at which testing occurred.	

Device Type	Location	Service	Time	Date	
Passed	
Auxiliary	
Releasing Device	Basement Corridor by Suite M20	Annual	3:51:48 PM	11/22/2022	
Releasing Device	Basement Corridor by Suite M20	Annual	3:51:55 PM	11/22/2022	
Releasing Device	1st Entrance from halfway to Oncology	Annual	11:41:40 AM	11/28/2022	
Releasing Device	1st Oncology Corridor	Annual	11:41:35 AM	11/28/2022	
Releasing Device	1st Oncology Corridor	Annual	11:41:45 AM	11/28/2022	
Releasing Device	2nd Corridor OB-GYN	Annual	5:29:51 PM	11/22/2022	
Control	
Annunciator	2nd Front Lobby	Annual	11:03:39 AM	11/21/2022	
Battery	Basement Dialer Above FACP	Annual	9:39:55 AM	11/21/2022	
Battery	1st Inside Transponder Panel Electrical rm	Annual	11:17:39 AM	11/21/2022	
Battery	1st Inside Transponder Panel Electrical rm	Annual	11:18:58 AM	11/21/2022	
Battery	2nd Front Lobby in Annunciator panel	Annual	11:03:42 AM	11/21/2022	
Battery	2nd Front Lobby in Annunciator panel	Annual	11:04:52 AM	11/21/2022	
Battery	2nd Inside Transponder Panel Electrical rm	Replaced	5:04:48 PM	11/22/2022	
Battery	2nd Inside Transponder Panel Electrical rm	Replaced	5:05:12 PM	11/22/2022	
Battery	3rd Inside Transponder Panel Electrical rm	Annual	10:28:33 AM	11/21/2022	
Battery	3rd Inside Transponder Panel Electrical rm	Annual	10:31:52 AM	11/21/2022	
Battery	3rd Internal Med South Electrical rm	Annual	10:38:20 AM	11/21/2022	
Battery	3rd Internal Med South Electrical rm	Annual	10:39:54 AM	11/21/2022	
Battery	4th Inside Transponder Panel Electrical	Annual	10:22:10 AM	11/21/2022	
Battery	4th Inside Transponder Panel Electrical	Annual	10:23:10 AM	11/21/2022	
Battery	5th Inside Transponder Panel Electrical rm 5112	Annual	10:01:49 AM	11/21/2022	
Battery	5th Inside Transponder Panel Electrical rm 5112	Annual	10:13:27 AM	11/21/2022	
Communicator	Basement Above FACP	Annual	9:34:53 AM	11/21/2022	
Control Panel	Basement Inside Electrical	Annual	9:34:50 AM	11/21/2022	
Expander Panel	1st Inside Electrical rm	Annual	10:10:08 AM	11/28/2022	
Expander Panel	2nd Inside Electrical rm	Annual	10:45:41 AM	11/21/2022	
Expander Panel	3rd Inside Electrical rm	Annual	10:28:31 AM	11/21/2022	
Expander Panel	4th Inside Electrical rm	Annual	10:20:42 AM	11/21/2022	
Expander Panel	5th Inside Electrical rm 5112	Annual	10:01:47 AM	11/21/2022	
Power Supply	1st Inside Electrical rm across hall from Suite 125	Annual	11:13:11 AM	11/21/2022	
Power Supply	3rd Inside Electrical rm Internal Med	Annual	10:38:18 AM	11/21/2022	
Indicating	
Speaker	Basement Digestive Health Corridor	Annual	3:57:52 PM	11/22/2022	
Speaker	Basement Family Medicine Suite Corridor by MH640	Annual	4:13:13 PM	11/22/2022	
Speaker	Basement Family Medicine Suite Corridor by MH652	Annual	4:06:45 PM	11/22/2022	
Speaker	Basement Urgent Care Suite Corridor	Annual	4:22:14 PM	11/22/2022	
Speaker	1st Oncology Corridor	Annual	9:56:53 AM	11/28/2022	
Speaker	1st Pharmacy Suite 180 Break rm	Annual	11:12:22 AM	11/28/2022	
Speaker	1st Pharmacy Suite 180 Ante rm Changing rm	Annual	11:12:17 AM	11/28/2022	
Speaker	2nd OB-GYN Corridor by Nurses Station	Annual	11:41:50 AM	11/28/2022	
Speaker	2nd OB-GYN Waiting Area	Annual	11:12:56 AM	11/28/2022	
Speaker	2nd ENT Corridor	Annual	11:41:55 AM	11/28/2022	
Speaker	3rd Corridor	Annual	12:08:07 PM	11/23/2022	
Speaker	3rd Corridor by Elevators	Annual	11:51:07 AM	11/23/2022	
Speaker	3rd Corridor to Hospital	Annual	12:07:38 PM	11/23/2022	
Speaker	3rd Internal Med Corridor	Annual	11:52:51 AM	11/23/2022	
Speaker	3rd Internal Med Corridor	Annual	11:53:42 AM	11/23/2022	
Speaker	3rd Internal Med Corridor	Annual	11:56:15 AM	11/23/2022	
Speaker	3rd Internal Med Corridor	Annual	11:58:45 AM	11/23/2022	
Speaker	3rd Internal Med Corridor	Annual	11:59:21 AM	11/23/2022	
Speaker	3rd Nephrology Suite 330 Corridor	Annual	12:03:15 PM	11/23/2022	
Speaker	3rd Nephrology Suite 330 Corridor	Annual	12:03:36 PM	11/23/2022	
Speaker	3rd Nephrology Suite 330 Corridor	Annual	12:04:34 PM	11/23/2022	
Speaker	4th Corridor	Annual	10:20:18 AM	11/23/2022	
Speaker	4th Corridor	Annual	10:25:33 AM	11/23/2022	
Speaker	4th Corridor	Annual	10:25:48 AM	11/23/2022	
Speaker	4th Elevator Lobby	Annual	9:58:52 AM	11/23/2022	
Speaker	4th Heart/Vascular Corridor	Annual	10:00:42 AM	11/23/2022	
Speaker	4th Heart/Vascular Corridor	Annual	10:02:45 AM	11/23/2022	
Speaker	4th Heart/Vascular Corridor	Annual	10:05:26 AM	11/23/2022	
Speaker	4th Heart/Vascular Heart Lab	Annual	10:11:01 AM	11/23/2022	
Speaker	4th Inside Stairwell A	Annual	5:26:45 PM	11/22/2022	
Speaker	4th Inside Stairwell B	Annual	10:01:30 AM	11/23/2022	
Speaker	4th Inside Stairwell C	Annual	10:17:36 AM	11/23/2022	
Speaker	4th Nuclear Med Corridor	Annual	10:17:44 AM	11/23/2022	
Speaker	4th Nuclear Med Corridor	Annual	10:18:57 AM	11/23/2022	
Speaker	4th Nuclear Med Corridor	Annual	10:19:04 AM	11/23/2022	
Speaker	5th Corridor	Annual	9:16:52 AM	11/23/2022	
Speaker	5th Corridor	Annual	9:32:15 AM	11/23/2022	
Speaker	5th Corridor	Annual	9:32:23 AM	11/23/2022	
Speaker	5th Corridor by Suite 500	Annual	9:29:23 AM	11/23/2022	
Speaker	5th Corridor in Suite 560	Annual	9:26:22 AM	11/23/2022	
Speaker	5th Elevator Lobby	Annual	9:08:41 AM	11/23/2022	
Speaker	5th Research Cardio Suite	Annual	9:23:14 AM	11/23/2022	
Speaker	5th Inside Stairwell B	Annual	9:10:23 AM	11/23/2022	
Speaker	5th Inside Stairwell C	Annual	9:19:23 AM	11/23/2022	
Speaker	5th Pulminary Corridor	Annual	9:09:27 AM	11/23/2022	
Speaker/Strobe	Basement Corridor	Annual	3:43:01 PM	11/22/2022	
Speaker/Strobe	Basement Corridor	Annual	3:51:44 PM	11/22/2022	
Speaker/Strobe	Basement Corridor by Stairway A	Repaired	2:12:40 PM	12/22/2022	
Speaker/Strobe	Basement Library	Annual	3:46:16 PM	11/22/2022	
Speaker/Strobe	Basement Library	Annual	3:46:31 PM	11/22/2022	
Speaker/Strobe	Basement Library manager office	Annual	3:46:24 PM	11/22/2022	
Speaker/Strobe	Basement Library next to manager office	Annual	3:47:23 PM	11/22/2022	
Speaker/Strobe	Basement Library training room	Annual	3:46:08 PM	11/22/2022	
Speaker/Strobe	Basement Media Center by Stair D	Annual	3:46:52 PM	11/22/2022	
Speaker/Strobe	Basement Clinical Education Corridor	Annual	3:43:48 PM	11/22/2022	
Speaker/Strobe	Basement Corridor by Digestive Health	Annual	3:55:02 PM	11/22/2022	
Speaker/Strobe	Basement Corridor to Hospital	Annual	11:42:00 AM	11/28/2022	
Speaker/Strobe	Basement Corridor by Clinical Learning Lab	Annual	5:35:57 PM	11/22/2022	
Speaker/Strobe	Basement Corridor by Colleague Health restroom	Annual	5:35:40 PM	11/22/2022	
Speaker/Strobe	Basement Corridor by Plant Engineering to Hospital	Annual	3:54:21 PM	11/22/2022	
Speaker/Strobe	Basement Old Lab	Repaired	2:12:29 PM	12/22/2022	
Speaker/Strobe	Basement Beside Electrical rm Corridor	Annual	3:42:31 PM	11/22/2022	
Speaker/Strobe	Basement Concourse Urgent Care Suite	Annual	4:21:37 PM	11/22/2022	
Speaker/Strobe	Basement Concourse Urgent Care Suite	Annual	4:21:52 PM	11/22/2022	
Speaker/Strobe	Basement Concourse Urgent Care Suite	Annual	4:22:26 PM	11/22/2022	
Speaker/Strobe	Basement Concourse Urgent Care Suite	Annual	4:23:37 PM	11/22/2022	
Speaker/Strobe	Basement Concourse Urgent Care Suite Registration	Annual	4:24:15 PM	11/22/2022	
Speaker/Strobe	Basement Concourse Urgent Care Suite Registration	Annual	4:24:25 PM	11/22/2022	
Speaker/Strobe	Basement Concourse Urgent Care Suite Waiting	Annual	4:04:39 PM	11/22/2022	
Speaker/Strobe	Basement Concourse in front of Elevators	Annual	4:03:59 PM	11/22/2022	
Speaker/Strobe	Basement Concourse in front of Registration	Annual	4:04:07 PM	11/22/2022	
Speaker/Strobe	Basement Concourse in front of Registration	Annual	4:04:20 PM	11/22/2022	
Speaker/Strobe	Basement Concourse in front of Registration	Annual	4:04:27 PM	11/22/2022	
Speaker/Strobe	Basement Concourse in front of Registration	Annual	4:04:34 PM	11/22/2022	
Speaker/Strobe	Basement Digestive Health Corridor	Annual	3:57:19 PM	11/22/2022	
Speaker/Strobe	Basement Digestive Health Corridor by Stairwell C	Annual	3:58:19 PM	11/22/2022	
Speaker/Strobe	Basement Digestive Health Restroom	Annual	3:56:08 PM	11/22/2022	
Speaker/Strobe	Basement Digestive Health Waiting area	Annual	3:55:59 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Corridor by MH631	Annual	4:05:32 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Corridor by MH637	Annual	4:05:39 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Corridor by MH642	Annual	4:07:12 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Corridor by MH646	Annual	4:05:46 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Corridor by MH648	Annual	4:07:00 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Corridor by MH658	Annual	4:06:02 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Inside MH644	Annual	4:07:29 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Inside MH658	Annual	4:05:57 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Waiting area	Annual	4:10:17 PM	11/22/2022	
Speaker/Strobe	Basement Family Medicine Suite C70 Waiting area	Annual	4:10:32 PM	11/22/2022	
Speaker/Strobe	Basement Inside Stairway A	Repaired	2:12:55 PM	12/22/2022	
Speaker/Strobe	Basement Inside Electrical Outside Entrance	Annual	10:51:26 AM	11/28/2022	
Speaker/Strobe	Basement Inside Electrical Outside Entrance	Annual	10:52:14 AM	11/28/2022	
Speaker/Strobe	Basement Library Distance Learning Center	Annual	3:47:53 PM	11/22/2022	
Speaker/Strobe	Basement Plant Engineering Corridor	Annual	3:52:54 PM	11/22/2022	
Speaker/Strobe	Basement Plant Engineering Corridor	Annual	3:53:12 PM	11/22/2022	
Speaker/Strobe	1st Corridor beside Stairway A	Annual	11:43:31 AM	11/28/2022	
Speaker/Strobe	1st Corridor by Suite 180	Annual	11:42:49 AM	11/28/2022	
Speaker/Strobe	1st Corridor to Hospital	Annual	11:42:52 AM	11/28/2022	
Speaker/Strobe	1st Corridor to Hospital	Annual	11:42:56 AM	11/28/2022	
Speaker/Strobe	1st Corridor by Neuroscience Suite 125	Annual	11:24:34 AM	11/28/2022	
Speaker/Strobe	1st Corridor by Performance Improvement	Annual	11:43:04 AM	11/28/2022	
Speaker/Strobe	1st Corridor in Neuroscience Suite 125	Annual	11:25:50 AM	11/28/2022	
Speaker/Strobe	1st Corridor in Neuroscience Suite 125	Annual	11:30:41 AM	11/28/2022	
Speaker/Strobe	1st Corridor in Neuroscience Suite 125	Annual	11:31:03 AM	11/28/2022	
Speaker/Strobe	1st Mechanical Electrical rm 1902	Annual	11:43:28 AM	11/28/2022	
Speaker/Strobe	1st Central Scheduling Corridor	Annual	11:43:08 AM	11/28/2022	
Speaker/Strobe	1st Diabetes Corridor	Annual	11:42:36 AM	11/28/2022	
Speaker/Strobe	1st Diabetes Corridor	Annual	11:42:40 AM	11/28/2022	
Speaker/Strobe	1st Diabetes Waiting rm	Annual	11:42:31 AM	11/28/2022	
Speaker/Strobe	1st Hyperbaric Wound Center Corridor	Annual	11:43:00 AM	11/28/2022	
Speaker/Strobe	1st Infusion Center Corridor	Annual	11:43:36 AM	11/28/2022	
Speaker/Strobe	1st Infusion Center Corridor	Annual	11:43:40 AM	11/28/2022	
Speaker/Strobe	1st Infusion Center Corridor	Annual	11:43:44 AM	11/28/2022	
Speaker/Strobe	1st Infusion Center Corridor	Annual	11:46:11 AM	11/28/2022	
Speaker/Strobe	1st Inside Stairwell A	Annual	11:47:21 AM	11/28/2022	
Speaker/Strobe	1st Inside Stairwell B	Annual	11:47:12 AM	11/28/2022	
Speaker/Strobe	1st Inside Stairwell C	Annual	11:47:08 AM	11/28/2022	
Speaker/Strobe	1st Oncology Corridor	Annual	9:47:46 AM	11/28/2022	
Speaker/Strobe	1st Oncology Corridor	Annual	11:42:05 AM	11/28/2022	
Speaker/Strobe	1st Oncology Corridor	Annual	11:42:13 AM	11/28/2022	
Speaker/Strobe	1st Oncology Corridor	Annual	11:42:24 AM	11/28/2022	
Speaker/Strobe	1st Oncology Corridor	Annual	11:42:28 AM	11/28/2022	
Speaker/Strobe	1st Oncology Register	Annual	11:42:10 AM	11/28/2022	
Speaker/Strobe	1st Oncology Stairwell D	Annual	11:47:24 AM	11/28/2022	
Speaker/Strobe	1st Performance Improvement Corridor	Annual	11:43:12 AM	11/28/2022	
Speaker/Strobe	1st Performance Improvement Corridor	Annual	11:43:16 AM	11/28/2022	
Speaker/Strobe	1st Performance Improvement Corridor	Annual	11:43:19 AM	11/28/2022	
Speaker/Strobe	1st Staff Elevator Lobby	Annual	11:43:24 AM	11/28/2022	
Speaker/Strobe	1st Suite 190 Corridor	Annual	11:42:45 AM	11/28/2022	
Speaker/Strobe	2nd Corridor by Pharmacy	Annual	11:08:14 AM	11/28/2022	
Speaker/Strobe	2nd Corridor by Stairwell B	Annual	11:11:33 AM	11/28/2022	
Speaker/Strobe	2nd Corridor by Suite 250	Annual	11:46:51 AM	11/28/2022	
Speaker/Strobe	2nd Corridor to Hospital	Annual	4:17:54 PM	11/22/2022	
Speaker/Strobe	2nd ENT Corridor	Annual	11:46:54 AM	11/28/2022	
Speaker/Strobe	2nd Mechanical rm	Annual	11:13:44 AM	11/28/2022	
Speaker/Strobe	2nd Mechanical rm	Annual	11:46:46 AM	11/28/2022	
Speaker/Strobe	2nd OB-GYN Corridor	Annual	11:46:25 AM	11/28/2022	
Speaker/Strobe	2nd OB-GYN Corridor	Annual	11:46:30 AM	11/28/2022	
Speaker/Strobe	2nd OB-GYN Corridor	Annual	11:46:38 AM	11/28/2022	
Speaker/Strobe	2nd OB-GYN Nurses Station	Annual	11:46:34 AM	11/28/2022	
Speaker/Strobe	2nd Optical	Annual	11:46:21 AM	11/28/2022	
Speaker/Strobe	2nd Pharmacy	Annual	11:46:16 AM	11/28/2022	
Speaker/Strobe	2nd ENT Corridor	Annual	11:46:58 AM	11/28/2022	
Speaker/Strobe	2nd Employee Staff Corridor	Annual	11:46:43 AM	11/28/2022	
Speaker/Strobe	2nd Front Lobby	Annual	11:07:43 AM	11/28/2022	
Speaker/Strobe	2nd Inside Stairwell A	Annual	11:47:17 AM	11/28/2022	
Speaker/Strobe	2nd Inside Stairwell B	Annual	11:11:53 AM	11/28/2022	
Speaker/Strobe	2nd Inside Stairwell C	Annual	11:47:02 AM	11/28/2022	
Speaker/Strobe	3rd Corridor Nephrology Suite 330	Annual	12:03:54 PM	11/23/2022	
Speaker/Strobe	3rd Corridor by Stairwell A	Annual	11:50:34 AM	11/23/2022	
Speaker/Strobe	3rd Corridor by Suite 340	Annual	12:07:55 PM	11/23/2022	
Speaker/Strobe	3rd Corridor for Internal Med by nurse station	Annual	11:51:58 AM	11/23/2022	
Speaker/Strobe	3rd Corridor to Hospital	Annual	12:00:52 PM	11/23/2022	
Speaker/Strobe	3rd Storage by Staff Corridor	Annual	12:10:01 PM	11/23/2022	
Speaker/Strobe	3rd Waiting area for Internal Med	Annual	11:51:43 AM	11/23/2022	
Speaker/Strobe	3rd Waiting rm Nephrology Suite 330	Annual	12:07:48 PM	11/23/2022	
Speaker/Strobe	3rd Employee Staff Corridor	Annual	11:49:22 AM	11/23/2022	
Speaker/Strobe	3rd Inside Stairwell A	Annual	11:50:56 AM	11/23/2022	
Speaker/Strobe	3rd Inside Stairwell B	Annual	11:54:44 AM	11/23/2022	
Speaker/Strobe	3rd Inside Stairwell C	Annual	12:02:43 PM	11/23/2022	
Speaker/Strobe	3rd Internal Med Corridor	Annual	11:55:29 AM	11/23/2022	
Speaker/Strobe	3rd Internal Med Corridor	Annual	11:57:57 AM	11/23/2022	
Speaker/Strobe	3rd Internal Med Corridor by Stair B	Annual	11:54:25 AM	11/23/2022	
Speaker/Strobe	3rd Internal Med Scheduling	Annual	12:00:05 PM	11/23/2022	
Speaker/Strobe	3rd Nephrology Suite 330 Corridor by Stair C	Annual	12:02:40 PM	11/23/2022	
Speaker/Strobe	3rd Storage Area across from staff Elevator	Annual	12:11:33 PM	11/23/2022	
Speaker/Strobe	3rd Suite 340 Corridor	Annual	12:05:14 PM	11/23/2022	
Speaker/Strobe	3rd Suite 340 Procedure rm	Annual	12:06:18 PM	11/23/2022	
Speaker/Strobe	4th Corridor	Annual	10:20:43 AM	11/23/2022	
Speaker/Strobe	4th Corridor by Heart/Vascular Registration	Annual	9:57:09 AM	11/23/2022	
Speaker/Strobe	4th Corridor by Stairwell A	Annual	9:57:53 AM	11/23/2022	
Speaker/Strobe	4th Corridor to Hospital	Annual	10:11:37 AM	11/23/2022	
Speaker/Strobe	4th Heart/Vascular Corridor	Annual	10:02:15 AM	11/23/2022	
Speaker/Strobe	4th Heart/Vascular Heart Lab	Annual	10:09:49 AM	11/23/2022	
Speaker/Strobe	4th Heart/Vascular Restroom	Annual	10:01:07 AM	11/23/2022	
Speaker/Strobe	4th Nuclear Waiting rm	Annual	10:20:05 AM	11/23/2022	
Speaker/Strobe	4th Staff Breakroom	Annual	10:23:54 AM	11/23/2022	
Speaker/Strobe	4th Waiting area for Heart/Vascular Registration	Annual	9:59:47 AM	11/23/2022	
Speaker/Strobe	4th Waiting area for Heart/Vascular Registration	Annual	9:59:52 AM	11/23/2022	
Speaker/Strobe	4th Employee Staff Corridor	Annual	9:56:29 AM	11/23/2022	
Speaker/Strobe	4th Heart/Vascular Corridor	Annual	10:08:28 AM	11/23/2022	
Speaker/Strobe	4th Inside Stairwell A	Annual	9:58:38 AM	11/23/2022	
Speaker/Strobe	4th Nuclear Med Corridor	Annual	10:17:09 AM	11/23/2022	
Speaker/Strobe	4th Nuclear Med Corridor	Annual	10:18:08 AM	11/23/2022	
Speaker/Strobe	4th Nuclear Med Corridor	Annual	10:21:42 AM	11/23/2022	
Speaker/Strobe	4th Nuclear Med Corridor	Annual	10:28:57 AM	11/23/2022	
Speaker/Strobe	5th Corridor	Annual	9:07:15 AM	11/23/2022	
Speaker/Strobe	5th Corridor	Annual	9:14:27 AM	11/23/2022	
Speaker/Strobe	5th Corridor	Annual	9:16:02 AM	11/23/2022	
Speaker/Strobe	5th Corridor	Annual	9:29:33 AM	11/23/2022	
Speaker/Strobe	5th Corridor	Annual	9:30:08 AM	11/23/2022	
Speaker/Strobe	5th Corridor by stairwell c	Annual	9:19:26 AM	11/23/2022	
Speaker/Strobe	5th Corridor in Suite 560	Annual	9:21:46 AM	11/23/2022	
Speaker/Strobe	5th Corridor in Suite 560	Annual	9:22:34 AM	11/23/2022	
Speaker/Strobe	5th Corridor in Suite 560	Annual	9:27:34 AM	11/23/2022	
Speaker/Strobe	5th Corridor to Hospital	Annual	9:17:52 AM	11/23/2022	
Speaker/Strobe	5th Office by Suite 500	Annual	9:30:51 AM	11/23/2022	
Speaker/Strobe	5th Beside Stairwell A	Annual	9:07:46 AM	11/23/2022	
Speaker/Strobe	5th Cardio Corridor	Annual	9:24:30 AM	11/23/2022	
Speaker/Strobe	5th Cardio Workroom	Annual	9:34:23 AM	11/23/2022	
Speaker/Strobe	5th Employee Staff Corridor	Annual	9:06:46 AM	11/23/2022	
Speaker/Strobe	5th Inside Stairwell A	Annual	9:02:32 AM	11/23/2022	
Speaker/Strobe	5th Pulminary Corridor by Stairwell B	Annual	9:10:00 AM	11/23/2022	
Speaker/Strobe	5th Pulminary Lobby	Annual	9:08:51 AM	11/23/2022	
Speaker/Strobe	5th Pulminary Lobby	Annual	9:09:16 AM	11/23/2022	
Speaker/Strobe	5th Pulminary outside break rm	Annual	9:13:08 AM	11/23/2022	
Speaker/Strobe	Penthouse	Annual	8:50:16 AM	11/23/2022	
Speaker/Strobe	Penthouse	Annual	8:52:11 AM	11/23/2022	
Speaker/Strobe	Penthouse Elevator room	Annual	8:49:47 AM	11/23/2022	
Speaker/Strobe	Penthouse top of Stair	Annual	8:48:31 AM	11/23/2022	
Strobe	Basement Vault	Annual	4:01:10 PM	11/22/2022	
Strobe	Basement Vault Storage rm	Annual	4:01:25 PM	11/22/2022	
Strobe	Basement vital care storage	Annual	3:49:22 PM	11/22/2022	
Strobe	Basement APOGEE Bathroom	Annual	3:49:57 PM	11/22/2022	
Strobe	Basement APOGEE Bathroom	Annual	3:50:12 PM	11/22/2022	
Strobe	Basement APOGEE Office	Annual	3:50:51 PM	11/22/2022	
Strobe	Basement APOGEE Office	Annual	3:50:57 PM	11/22/2022	
Strobe	Basement APOGEE Office	Annual	3:51:02 PM	11/22/2022	
Strobe	Basement Corridor	Annual	3:51:04 PM	11/22/2022	
Strobe	Basement Corridor by Suite M20	Annual	3:52:01 PM	11/22/2022	
Strobe	Basement Corridor by Plant Engineering to Hospital	Annual	3:54:07 PM	11/22/2022	
Strobe	Basement Family Medicine Suite Restroom	Annual	4:07:58 PM	11/22/2022	
Strobe	Basement Family Medicine Suite Restroom	Annual	4:08:59 PM	11/22/2022	
Strobe	Basement Family Medicine Suite inside MH657	Annual	4:09:09 PM	11/22/2022	
Strobe	Basement Janitors Closet by Stairwell	Annual	3:42:59 PM	11/22/2022	
Strobe	Basement Lab janitors Closet	Annual	1:08:06 PM	11/21/2022	
Strobe	Basement Lab waiting rm	Annual	4:02:06 PM	11/22/2022	
Strobe	Basement Lab Mens Bathroom	Annual	4:02:37 PM	11/22/2022	
Strobe	Basement Lab womens restroom	Annual	4:02:17 PM	11/22/2022	
Strobe	Basement Library	Annual	11:47:41 AM	11/28/2022	
Strobe	Basement Office Chief Medical Info Officer	Annual	3:45:43 PM	11/22/2022	
Strobe	Basement Office Multimedia Technology Specialist	Annual	11:47:38 AM	11/28/2022	
Strobe	Basement Office Multimedia Technology Specialist storage	Annual	3:49:03 PM	11/22/2022	
Strobe	Basement Vault Sprinkler rm	Annual	4:01:35 PM	11/22/2022	
Strobe	Basement Waiting Area	Annual	3:49:36 PM	11/22/2022	
Strobe	Basement Beside Stairwell	Annual	3:43:08 PM	11/22/2022	
Strobe	Basement Colleague Health Restroom	Annual	12:25:07 PM	11/28/2022	
Strobe	Basement Colleague Health Restroom	Annual	12:27:51 PM	11/28/2022	
Strobe	Basement Colleague Health Training rm	Annual	12:25:02 PM	11/28/2022	
Strobe	Basement Colleague Health Waiting/Sleep rm M20-A	Annual	12:27:55 PM	11/28/2022	
Strobe	Basement Concourse Family Medicine Suite inside MH636	Annual	4:08:24 PM	11/22/2022	
Strobe	Basement Concourse Family Medicine Suite inside MH646	Annual	4:09:19 PM	11/22/2022	
Strobe	Basement Concourse Urgent Care Suite Restroom	Annual	4:21:56 PM	11/22/2022	
Strobe	Basement Digestive Health Break rm	Annual	3:58:04 PM	11/22/2022	
Strobe	Basement Digestive Health Corridor	Annual	3:56:12 PM	11/22/2022	
Strobe	Basement Digestive Health Exam rm	Annual	3:57:04 PM	11/22/2022	
Strobe	Basement Digestive Health Exam rm	Annual	3:58:54 PM	11/22/2022	
Strobe	Basement Digestive Health Exam rm	Annual	3:59:07 PM	11/22/2022	
Strobe	Basement Digestive Health Exam rm	Annual	3:59:11 PM	11/22/2022	
Strobe	Basement Digestive Health Exam rm	Annual	3:59:15 PM	11/22/2022	
Strobe	Basement Digestive Health Lab area	Annual	3:56:37 PM	11/22/2022	
Strobe	Basement Digestive Health Office	Annual	3:56:45 PM	11/22/2022	
Strobe	Basement Digestive Health Office	Annual	3:57:23 PM	11/22/2022	
Strobe	Basement Digestive Health Office	Annual	3:57:28 PM	11/22/2022	
Strobe	Basement Digestive Health Office	Annual	3:57:33 PM	11/22/2022	
Strobe	Basement Digestive Health Office	Annual	3:57:38 PM	11/22/2022	
Strobe	Basement Digestive Health Office	Annual	3:57:50 PM	11/22/2022	
Strobe	Basement Digestive Health Office	Annual	3:58:43 PM	11/22/2022	
Strobe	Basement Digestive Health Office	Annual	12:27:47 PM	11/28/2022	
Strobe	Basement Digestive Health Restroom	Annual	3:56:31 PM	11/22/2022	
Strobe	Basement Digestive Health Restroom	Annual	3:58:23 PM	11/22/2022	
Strobe	Basement Digestive Health Supply	Annual	3:57:45 PM	11/22/2022	
Strobe	Basement Family Medicine Suite Inside MH646 Clean Supply	Annual	4:08:49 PM	11/22/2022	
Strobe	Basement Inside Clinical Education	Annual	3:43:41 PM	11/22/2022	
Strobe	Basement Inside Clinical Education Office	Annual	3:43:53 PM	11/22/2022	
Strobe	Basement Inside Clinical Education Office	Annual	3:43:57 PM	11/22/2022	
Strobe	Basement Inside Clinical Education Office	Annual	3:44:52 PM	11/22/2022	
Strobe	Basement Inside Clinical Education Office	Annual	3:47:49 PM	11/22/2022	
Strobe	Basement Inside Clinical Education Office distance learning	Annual	3:47:58 PM	11/22/2022	
Strobe	Basement Inside Clinical Education Office mechanical rm 105	Annual	3:48:12 PM	11/22/2022	
Strobe	Basement Inside Clinical Education Office mechanical rm 106	Annual	9:09:28 AM	11/28/2022	
Strobe	Basement Inside Clinical Learning Lab	Annual	3:43:17 PM	11/22/2022	
Strobe	Basement Inside Clinical Learning Lab	Annual	3:43:25 PM	11/22/2022	
Strobe	Basement Inside Clinical Learning Lab office	Annual	3:43:30 PM	11/22/2022	
Strobe	Basement Inside Electrical by Fire Panel	Annual	3:42:24 PM	11/22/2022	
Strobe	Basement Inside Stairwell C	Annual	3:58:28 PM	11/22/2022	
Strobe	Basement Inside Telephone rm by Hospital corridor	Annual	9:41:51 AM	11/28/2022	
Strobe	Basement Old Lab	Annual	4:02:51 PM	11/22/2022	
Strobe	Basement Old Lab reception	Annual	11:47:46 AM	11/28/2022	
Strobe	Basement Old Lab Restroom	Annual	4:03:07 PM	11/22/2022	
Strobe	Basement Old Lab child’s room	Annual	4:03:01 PM	11/22/2022	
Strobe	Basement Old Lab drawing station	Annual	1:05:39 PM	11/21/2022	
Strobe	Basement Plant Engineering Conference	Annual	3:53:02 PM	11/22/2022	
Strobe	Basement Plant Engineering Conference	Annual	3:53:05 PM	11/22/2022	
Strobe	Basement Plant Engineering Office	Annual	3:52:39 PM	11/22/2022	
Strobe	Basement Plant Engineering Office	Annual	3:53:15 PM	11/22/2022	
Strobe	Basement Plant Engineering Office	Annual	3:53:19 PM	11/22/2022	
Strobe	Basement Plant Engineering Office	Annual	3:53:25 PM	11/22/2022	
Strobe	Basement Plant Engineering Office	Annual	3:53:44 PM	11/22/2022	
Strobe	Basement Plant Engineering Office	Annual	3:53:51 PM	11/22/2022	
Strobe	Basement Plant Engineering Office	Annual	3:53:55 PM	11/22/2022	
Strobe	Basement Staff Bathroom by Fire Panel	Annual	3:42:51 PM	11/22/2022	
Strobe	Basement Vault Break rm	Annual	4:00:40 PM	11/22/2022	
Strobe	1st Cancer Registry Office	Annual	12:15:31 PM	11/28/2022	
Strobe	1st Conference Resource rm oncology ed	Annual	12:15:38 PM	11/28/2022	
Strobe	1st Corridor by Neuroscience Suite 125	Annual	12:13:01 PM	11/28/2022	
Strobe	1st Elevator Lobby	Annual	12:26:26 PM	11/28/2022	
Strobe	1st Mens Restroom by Stair A	Annual	12:15:50 PM	11/28/2022	
Strobe	1st Pharmacy Suite 180	Annual	12:28:17 PM	11/28/2022	
Strobe	1st Restroom by Central Scheduling	Annual	12:14:11 PM	11/28/2022	
Strobe	1st Restroom by Central Scheduling	Annual	12:14:16 PM	11/28/2022	
Strobe	1st Womens Restroom by Stair A	Annual	12:15:46 PM	11/28/2022	
Strobe	1st Central Scheduling	Annual	12:14:40 PM	11/28/2022	
Strobe	1st Central Scheduling Break rm	Annual	12:14:22 PM	11/28/2022	
Strobe	1st Central Scheduling Office	Annual	12:14:27 PM	11/28/2022	
Strobe	1st Diabetes Coat rm	Annual	12:05:34 PM	11/28/2022	
Strobe	1st Diabetes Exam rm	Annual	12:03:03 PM	11/28/2022	
Strobe	1st Diabetes Exam rm	Annual	12:03:13 PM	11/28/2022	
Strobe	1st Diabetes File room	Annual	12:03:47 PM	11/28/2022	
Strobe	1st Diabetes Kitchen	Annual	12:03:17 PM	11/28/2022	
Strobe	1st Diabetes Office	Annual	12:03:30 PM	11/28/2022	
Strobe	1st Diabetes Office	Annual	12:03:34 PM	11/28/2022	
Strobe	1st Diabetes Office	Annual	12:05:03 PM	11/28/2022	
Strobe	1st Diabetes Office	Annual	12:05:07 PM	11/28/2022	
Strobe	1st Diabetes Office	Annual	12:05:30 PM	11/28/2022	
Strobe	1st Diabetes Office	Annual	12:05:38 PM	11/28/2022	
Strobe	1st Diabetes Restroom	Annual	12:04:33 PM	11/28/2022	
Strobe	1st Diabetes Supply	Annual	12:03:59 PM	11/28/2022	
Strobe	1st Diabetes exam rm	Annual	12:03:26 PM	11/28/2022	
Strobe	1st Hyperbaric Wound Center Changing rm	Annual	12:23:39 PM	11/28/2022	
Strobe	1st Hyperbaric Wound Center Exam rm	Annual	12:12:43 PM	11/28/2022	
Strobe	1st Hyperbaric Wound Center Exam rm	Annual	12:12:58 PM	11/28/2022	
Strobe	1st Hyperbaric Wound Center Exam rm	Annual	12:24:45 PM	11/28/2022	
Strobe	1st Hyperbaric Wound Center Locker rm	Annual	11:31:54 AM	11/28/2022	
Strobe	1st Hyperbaric Wound Center Office	Annual	12:24:49 PM	11/28/2022	
Strobe	1st Hyperbaric Wound Center Waiting rm	Annual	11:31:51 AM	11/28/2022	
Strobe	1st I T closet by Cancer Registry Office	Annual	12:15:35 PM	11/28/2022	
Strobe	1st Infectious Diseases Bathroom	Annual	12:09:46 PM	11/28/2022	
Strobe	1st Infectious Diseases Bathroom	Annual	12:11:21 PM	11/28/2022	
Strobe	1st Infectious Diseases Corridor	Annual	12:09:37 PM	11/28/2022	
Strobe	1st Infectious Diseases Exam rm	Annual	12:09:32 PM	11/28/2022	
Strobe	1st Infectious Diseases Med rm	Annual	12:12:13 PM	11/28/2022	
Strobe	1st Infectious Diseases Waiting rm	Annual	12:28:00 PM	11/28/2022	
Strobe	1st Infectious Diseases exam rm	Annual	12:10:00 PM	11/28/2022	
Strobe	1st Infectious Diseases exam rm	Annual	12:10:05 PM	11/28/2022	
Strobe	1st Infectious Diseases exam rm	Annual	12:10:08 PM	11/28/2022	
Strobe	1st Infectious Diseases exam rm	Annual	12:10:41 PM	11/28/2022	
Strobe	1st Infectious Diseases exam rm	Annual	12:10:46 PM	11/28/2022	
Strobe	1st Infectious Diseases exam rm	Annual	12:10:50 PM	11/28/2022	
Strobe	1st Infectious Diseases exam rm	Annual	12:11:47 PM	11/28/2022	
Strobe	1st Infectious Diseases exam rm	Annual	12:11:56 PM	11/28/2022	
Strobe	1st Infectious Diseases my stairwell c	Annual	12:11:24 PM	11/28/2022	
Strobe	1st Infectious Diseases nurses area	Annual	12:09:02 PM	11/28/2022	
Strobe	1st Infectious Diseases nurses area	Annual	12:09:42 PM	11/28/2022	
Strobe	1st Infectious Diseases office	Annual	12:10:54 PM	11/28/2022	
Strobe	1st Infectious Diseases office	Annual	12:10:58 PM	11/28/2022	
Strobe	1st Infectious Diseases office	Annual	12:11:17 PM	11/28/2022	
Strobe	1st Infectious Diseases office	Annual	12:11:28 PM	11/28/2022	
Strobe	1st Infectious Diseases office	Annual	12:11:32 PM	11/28/2022	
Strobe	1st Infectious Diseases office	Annual	12:11:39 PM	11/28/2022	
Strobe	1st Infectious Diseases office	Annual	12:11:43 PM	11/28/2022	
Strobe	1st Infectious Diseases office Corridor	Annual	12:11:35 PM	11/28/2022	
Strobe	1st Infectious Diseases storage rm	Annual	12:09:55 PM	11/28/2022	
Strobe	1st Infectious Diseases supply lunch rm	Annual	12:12:00 PM	11/28/2022	
Strobe	1st Infectious Diseases supply lunch rm	Annual	12:12:04 PM	11/28/2022	
Strobe	1st Infectious Diseases supply lunch rm	Annual	12:12:10 PM	11/28/2022	
Strobe	1st Infectious Diseases supply lunch rm	Annual	12:28:04 PM	11/28/2022	
Strobe	1st Infusion Center Break rm	Annual	12:26:35 PM	11/28/2022	
Strobe	1st Infusion Center Corridor	Annual	12:25:19 PM	11/28/2022	
Strobe	1st Infusion Center Lab draw rm	Annual	12:25:33 PM	11/28/2022	
Strobe	1st Infusion Center Office	Annual	12:25:47 PM	11/28/2022	
Strobe	1st Infusion Center Patient care rm	Annual	12:25:51 PM	11/28/2022	
Strobe	1st Infusion Center Restroom	Annual	12:25:37 PM	11/28/2022	
Strobe	1st Infusion Center Restroom	Annual	12:25:42 PM	11/28/2022	
Strobe	1st Infusion Center Supply rm	Annual	12:25:23 PM	11/28/2022	
Strobe	1st Infusion Center Waiting rm	Annual	12:25:28 PM	11/28/2022	
Strobe	1st Inside Electrical rm by Transponder	Annual	12:12:17 PM	11/28/2022	
Strobe	1st Janitors Closet by Central Scheduling	Annual	12:31:43 PM	11/21/2022	
Strobe	1st Neuroscience Suite 125 Break rm	Annual	11:31:08 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Exam rm	Annual	11:25:39 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Exam rm	Annual	11:25:43 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Exam rm	Annual	11:25:52 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Exam rm	Annual	11:25:56 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Exam rm	Annual	11:30:44 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Exam rm	Annual	11:30:54 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Exam rm	Annual	12:13:43 PM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Exam rm 10 bathroom	Annual	12:13:56 PM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Office	Annual	11:25:30 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Office	Annual	11:26:04 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Office	Annual	11:26:11 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Office	Annual	11:26:19 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Office	Annual	11:26:24 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Office	Annual	11:26:30 AM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Restroom	Annual	12:13:07 PM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Restroom	Annual	12:13:38 PM	11/28/2022	
Strobe	1st Neuroscience Suite 125 Restroom	Annual	12:13:48 PM	11/28/2022	
Strobe	1st Oncology Break rm	Annual	9:57:01 AM	11/28/2022	
Strobe	1st Oncology Conference rm	Annual	12:05:25 PM	11/28/2022	
Strobe	1st Oncology Exam rm	Annual	11:54:44 AM	11/28/2022	
Strobe	1st Oncology Exam rm	Annual	11:56:28 AM	11/28/2022	
Strobe	1st Oncology Exam rm	Annual	11:56:33 AM	11/28/2022	
Strobe	1st Oncology Exam rm	Annual	11:56:37 AM	11/28/2022	
Strobe	1st Oncology Exam rm	Annual	11:56:41 AM	11/28/2022	
Strobe	1st Oncology Exam rm	Annual	11:56:46 AM	11/28/2022	
Strobe	1st Oncology Exam rm	Annual	11:56:50 AM	11/28/2022	
Strobe	1st Oncology Exam rm	Annual	11:56:54 AM	11/28/2022	
Strobe	1st Oncology Exam rm	Annual	11:57:02 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	9:48:04 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	9:48:08 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	10:00:30 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	11:47:55 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	11:48:02 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	11:54:16 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	11:54:20 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	11:54:24 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	11:54:28 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	11:54:35 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	11:56:19 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	11:56:58 AM	11/28/2022	
Strobe	1st Oncology Office	Annual	12:02:54 PM	11/28/2022	
Strobe	1st Oncology Office	Annual	12:02:59 PM	11/28/2022	
Strobe	1st Oncology Office	Annual	12:05:12 PM	11/28/2022	
Strobe	1st Oncology Office	Annual	12:05:16 PM	11/28/2022	
Strobe	1st Oncology Office	Annual	12:08:56 PM	11/28/2022	
Strobe	1st Oncology Reception	Annual	11:56:10 AM	11/28/2022	
Strobe	1st Oncology Reception	Annual	11:56:15 AM	11/28/2022	
Strobe	1st Oncology Restroom	Annual	9:47:51 AM	11/28/2022	
Strobe	1st Oncology Restroom	Annual	11:47:50 AM	11/28/2022	
Strobe	1st Oncology Restroom	Annual	11:52:58 AM	11/28/2022	
Strobe	1st Oncology Storage Closet	Annual	9:56:40 AM	11/28/2022	
Strobe	1st Oncology Supply Closet	Annual	11:54:48 AM	11/28/2022	
Strobe	1st Oncology Waiting rm	Annual	11:56:23 AM	11/28/2022	
Strobe	1st Oncology Waiting rm Restroom	Annual	9:57:40 AM	11/28/2022	
Strobe	1st Performance Improvement Office	Annual	12:15:12 PM	11/28/2022	
Strobe	1st Performance Improvement Office	Annual	12:15:15 PM	11/28/2022	
Strobe	1st Performance Improvement Office	Annual	12:15:20 PM	11/28/2022	
Strobe	1st Performance Improvement Office	Annual	12:15:26 PM	11/28/2022	
Strobe	1st Pharmacy Suite 180 Break rm	Annual	12:37:33 PM	11/28/2022	
Strobe	1st Pharmacy Suite 180 Ante rm Changing rm	Annual	12:37:24 PM	11/28/2022	
Strobe	1st Pharmacy Suite 180 Hazardous drugs tag on Strobe in Lobby	Annual	12:37:20 PM	11/28/2022	
Strobe	1st Pharmacy Suite 180 IV rm tag on Strobe in Ante rm	Annual	12:37:28 PM	11/28/2022	
Strobe	1st Suite 190 Exam rm	Annual	12:05:42 PM	11/28/2022	
Strobe	1st Suite 190 Exam rm	Annual	12:05:46 PM	11/28/2022	
Strobe	1st Suite 190 Office	Annual	12:05:50 PM	11/28/2022	
Strobe	1st Suite 190 Office	Annual	12:08:46 PM	11/28/2022	
Strobe	1st Suite 190 Office	Annual	12:08:52 PM	11/28/2022	
Strobe	1st Suite 190 Restroom	Annual	12:05:54 PM	11/28/2022	
Strobe	2nd Behavioral Services Suite 208	Annual	12:15:58 PM	11/28/2022	
Strobe	2nd Behavioral Services Suite 208	Annual	12:16:09 PM	11/28/2022	
Strobe	2nd Behavioral Services Suite 208	Annual	12:16:28 PM	11/28/2022	
Strobe	2nd OB-GYN Break Room	Annual	12:21:41 PM	11/28/2022	
Strobe	2nd OB-GYN Dr Office	Annual	12:20:17 PM	11/28/2022	
Strobe	2nd OB-GYN Dr Office	Annual	12:20:21 PM	11/28/2022	
Strobe	2nd OB-GYN Dr Office	Annual	12:20:33 PM	11/28/2022	
Strobe	2nd OB-GYN Dr Office	Annual	12:20:44 PM	11/28/2022	
Strobe	2nd OB-GYN Dr Office	Annual	12:20:52 PM	11/28/2022	
Strobe	2nd OB-GYN Dr Office	Annual	12:20:56 PM	11/28/2022	
Strobe	2nd OB-GYN Dr Office	Annual	12:21:29 PM	11/28/2022	
Strobe	2nd OB-GYN Dr Office	Annual	12:21:37 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:16:05 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:16:19 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:16:23 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:16:33 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:16:58 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:17:03 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:17:07 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:17:11 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:17:25 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:18:00 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:18:04 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:18:12 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:18:22 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:18:25 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:18:29 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:20:05 PM	11/28/2022	
Strobe	2nd OB-GYN Exam Rm	Annual	12:24:54 PM	11/28/2022	
Strobe	2nd OB-GYN Lab	Annual	12:20:09 PM	11/28/2022	
Strobe	2nd OB-GYN Reception	Annual	12:20:48 PM	11/28/2022	
Strobe	2nd OB-GYN Restroom	Annual	12:16:41 PM	11/28/2022	
Strobe	2nd OB-GYN Restroom	Annual	12:17:15 PM	11/28/2022	
Strobe	2nd OB-GYN Restroom	Annual	12:18:07 PM	11/28/2022	
Strobe	2nd OB-GYN Restroom	Annual	12:20:13 PM	11/28/2022	
Strobe	2nd OB-GYN Supply rm	Annual	12:21:33 PM	11/28/2022	
Strobe	2nd OB-GYN Supply rm by Lab	Annual	12:16:38 PM	11/28/2022	
Strobe	2nd OB-GYN Ultra Sound rm	Annual	12:16:50 PM	11/28/2022	
Strobe	2nd OB-GYN Ultra Sound rm	Annual	12:28:08 PM	11/28/2022	
Strobe	2nd OB-GYN Waiting Rm	Annual	11:12:51 AM	11/28/2022	
Strobe	2nd Optical	Annual	10:56:26 AM	11/28/2022	
Strobe	2nd Optical Office	Annual	12:21:45 PM	11/28/2022	
Strobe	2nd Optometrist office	Annual	12:16:01 PM	11/28/2022	
Strobe	2nd Pharmacy Break Room	Annual	12:28:22 PM	11/28/2022	
Strobe	2nd Pharmacy Office	Annual	12:26:39 PM	11/28/2022	
Strobe	2nd Restroom by Stairwell B	Annual	11:11:31 AM	11/28/2022	
Strobe	2nd ENT Allergy Clinic	Annual	12:23:32 PM	11/28/2022	
Strobe	2nd ENT Billing rm	Annual	12:22:49 PM	11/28/2022	
Strobe	2nd ENT Break room	Annual	12:23:16 PM	11/28/2022	
Strobe	2nd ENT Dr Office	Annual	12:21:58 PM	11/28/2022	
Strobe	2nd ENT Dr Office	Annual	12:22:03 PM	11/28/2022	
Strobe	2nd ENT Dr Office	Annual	12:22:14 PM	11/28/2022	
Strobe	2nd ENT Dr Office	Annual	12:22:57 PM	11/28/2022	
Strobe	2nd ENT Dr Office	Annual	12:23:01 PM	11/28/2022	
Strobe	2nd ENT Dr office	Annual	12:23:12 PM	11/28/2022	
Strobe	2nd ENT Exam rm	Annual	12:22:07 PM	11/28/2022	
Strobe	2nd ENT Exam rm	Annual	12:22:18 PM	11/28/2022	
Strobe	2nd ENT Exam rm	Annual	12:22:22 PM	11/28/2022	
Strobe	2nd ENT Exam rm	Annual	12:22:26 PM	11/28/2022	
Strobe	2nd ENT Exam rm	Annual	12:22:31 PM	11/28/2022	
Strobe	2nd ENT Exam rm	Annual	12:22:35 PM	11/28/2022	
Strobe	2nd ENT File rm	Annual	12:22:53 PM	11/28/2022	
Strobe	2nd ENT File rm	Annual	12:23:20 PM	11/28/2022	
Strobe	2nd ENT Manager office	Annual	12:23:27 PM	11/28/2022	
Strobe	2nd ENT Nurses Station	Annual	12:24:58 PM	11/28/2022	
Strobe	2nd ENT Restroom	Annual	12:22:46 PM	11/28/2022	
Strobe	2nd ENT Restroom	Annual	12:23:06 PM	11/28/2022	
Strobe	2nd ENT Supply rm	Annual	12:23:35 PM	11/28/2022	
Strobe	2nd Inside Mens Lobby Restroom	Annual	12:26:22 PM	11/28/2022	
Strobe	2nd Waiting rm Suite 250	Annual	12:21:49 PM	11/28/2022	
Strobe	2nd Women's Restroom in Lobby	Annual	12:26:30 PM	11/28/2022	
Strobe	3rd Corridor By Internal Med	Annual	12:08:13 PM	11/23/2022	
Strobe	3rd Mens Restroom	Annual	11:50:02 AM	11/23/2022	
Strobe	3rd Office 320	Annual	12:08:50 PM	11/23/2022	
Strobe	3rd Staff Corridor Restroom	Annual	11:49:16 AM	11/23/2022	
Strobe	3rd Staff Corridor Storage Restroom	Annual	12:09:05 PM	11/23/2022	
Strobe	3rd Womens Restroom	Annual	11:50:25 AM	11/23/2022	
Strobe	3rd Internal Med Conference rm	Annual	11:53:58 AM	11/23/2022	
Strobe	3rd Internal Med Draw Station	Annual	11:58:51 AM	11/23/2022	
Strobe	3rd Internal Med Draw Station Lab	Annual	11:59:41 AM	11/23/2022	
Strobe	3rd Internal Med Exam 1	Annual	11:53:18 AM	11/23/2022	
Strobe	3rd Internal Med Exam 10	Annual	11:55:27 AM	11/23/2022	
Strobe	3rd Internal Med Exam 11	Annual	11:55:43 AM	11/23/2022	
Strobe	3rd Internal Med Exam 12	Annual	11:55:37 AM	11/23/2022	
Strobe	3rd Internal Med Exam 14	Annual	11:56:23 AM	11/23/2022	
Strobe	3rd Internal Med Exam 15	Annual	11:56:47 AM	11/23/2022	
Strobe	3rd Internal Med Exam 16	Annual	11:56:52 AM	11/23/2022	
Strobe	3rd Internal Med Exam 17	Annual	11:56:58 AM	11/23/2022	
Strobe	3rd Internal Med Exam 19	Annual	12:10:41 PM	11/23/2022	
Strobe	3rd Internal Med Exam 2	Annual	11:53:35 AM	11/23/2022	
Strobe	3rd Internal Med Exam 20	Annual	11:57:43 AM	11/23/2022	
Strobe	3rd Internal Med Exam 21	Annual	11:58:19 AM	11/23/2022	
Strobe	3rd Internal Med Exam 22	Annual	11:58:25 AM	11/23/2022	
Strobe	3rd Internal Med Exam 23	Annual	11:58:32 AM	11/23/2022	
Strobe	3rd Internal Med Exam 24	Annual	12:10:47 PM	11/23/2022	
Strobe	3rd Internal Med Exam 26	Annual	11:58:41 AM	11/23/2022	
Strobe	3rd Internal Med Exam 26	Annual	12:11:10 PM	11/23/2022	
Strobe	3rd Internal Med Exam 30	Annual	12:00:14 PM	11/23/2022	
Strobe	3rd Internal Med Exam 31	Annual	12:10:54 PM	11/23/2022	
Strobe	3rd Internal Med Exam 5	Annual	12:10:24 PM	11/23/2022	
Strobe	3rd Internal Med Exam 6	Annual	12:10:28 PM	11/23/2022	
Strobe	3rd Internal Med Exam 7	Annual	11:55:05 AM	11/23/2022	
Strobe	3rd Internal Med Exam 8	Annual	11:55:16 AM	11/23/2022	
Strobe	3rd Internal Med Exam 9	Annual	11:55:21 AM	11/23/2022	
Strobe	3rd Internal Med Flex 1	Annual	11:52:32 AM	11/23/2022	
Strobe	3rd Internal Med Flex 2	Annual	11:53:23 AM	11/23/2022	
Strobe	3rd Internal Med Medical Records	Annual	11:53:49 AM	11/23/2022	
Strobe	3rd Internal Med Medical Supply	Annual	12:10:35 PM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:54:08 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:54:14 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:54:57 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:55:11 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:55:33 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:55:50 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:56:41 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:57:30 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:57:36 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:57:47 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:57:53 AM	11/23/2022	
Strobe	3rd Internal Med Office	Annual	11:59:56 AM	11/23/2022	
Strobe	3rd Internal Med Restroom	Annual	11:57:07 AM	11/23/2022	
Strobe	3rd Internal Med Restroom	Annual	11:59:11 AM	11/23/2022	
Strobe	3rd Internal Med Restroom by Stair B	Annual	11:54:27 AM	11/23/2022	
Strobe	3rd Internal Med Restroom by exam 30	Annual	12:00:20 PM	11/23/2022	
Strobe	3rd Internal Med Soiled Utility	Annual	11:52:26 AM	11/23/2022	
Strobe	3rd Internal Med Storage rm	Annual	11:59:02 AM	11/23/2022	
Strobe	3rd Internal Med Supply	Annual	11:59:18 AM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Break area	Annual	12:03:10 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Corridor	Annual	12:04:32 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Exam 1	Annual	12:02:05 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Exam 1	Annual	12:04:12 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Exam 2	Annual	12:02:00 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Exam 2	Annual	12:03:45 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Exam 3	Annual	12:03:39 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Exam 3A	Annual	12:02:16 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Nurse station storage	Annual	12:02:11 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Office	Annual	12:03:19 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Office	Annual	12:03:27 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Office	Annual	12:04:18 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Office	Annual	12:04:26 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Restroom	Annual	12:03:04 PM	11/23/2022	
Strobe	3rd Nephrology Suite 330 Supply	Annual	12:02:28 PM	11/23/2022	
Strobe	3rd Office across from Mens Restroom	Annual	11:51:20 AM	11/23/2022	
Strobe	3rd Suite 340 Reception	Annual	12:07:17 PM	11/23/2022	
Strobe	3rd Suite 340 Corridor	Annual	12:06:07 PM	11/23/2022	
Strobe	3rd Suite 340 Exam rm	Annual	12:05:10 PM	11/23/2022	
Strobe	3rd Suite 340 Exam rm	Annual	12:05:17 PM	11/23/2022	
Strobe	3rd Suite 340 Exam rm 1	Annual	12:04:57 PM	11/23/2022	
Strobe	3rd Suite 340 Office	Annual	12:04:42 PM	11/23/2022	
Strobe	3rd Suite 340 Photo rm	Annual	12:05:04 PM	11/23/2022	
Strobe	3rd Suite 340 Procedure rm	Annual	12:06:34 PM	11/23/2022	
Strobe	3rd Suite 340 Procedure rm Restroom	Annual	12:06:39 PM	11/23/2022	
Strobe	3rd Suite 340 Restroom	Annual	12:04:50 PM	11/23/2022	
Strobe	3rd Suite 340 Waiting rm	Annual	12:05:55 PM	11/23/2022	
Strobe	4th Staff Breakroom	Annual	10:24:19 AM	11/23/2022	
Strobe	4th Staff Breakroom	Annual	10:24:29 AM	11/23/2022	
Strobe	4th Staff Breakroom Restroom	Annual	10:24:09 AM	11/23/2022	
Strobe	4th Staff Conference training	Annual	10:23:36 AM	11/23/2022	
Strobe	4th Staff Conference training	Annual	10:29:47 AM	11/23/2022	
Strobe	4th Corridor by staff breakroom	Annual	10:29:39 AM	11/23/2022	
Strobe	4th Mens Restroom	Annual	9:57:33 AM	11/23/2022	
Strobe	4th Womens Restroom	Annual	9:58:07 AM	11/23/2022	
Strobe	4th Family Restroom	Annual	10:20:30 AM	11/23/2022	
Strobe	4th Heart/Vascular CT Surgery rm	Annual	10:09:09 AM	11/23/2022	
Strobe	4th Heart/Vascular Corridor	Annual	10:01:50 AM	11/23/2022	
Strobe	4th Heart/Vascular Dr Office	Annual	9:59:20 AM	11/23/2022	
Strobe	4th Heart/Vascular Dr Office	Annual	10:04:50 AM	11/23/2022	
Strobe	4th Heart/Vascular Dr Office	Annual	10:05:18 AM	11/23/2022	
Strobe	4th Heart/Vascular Dr Office	Annual	10:05:23 AM	11/23/2022	
Strobe	4th Heart/Vascular Dr Office	Annual	10:05:32 AM	11/23/2022	
Strobe	4th Heart/Vascular Dr Office	Annual	10:05:43 AM	11/23/2022	
Strobe	4th Heart/Vascular Dr Office	Annual	10:05:53 AM	11/23/2022	
Strobe	4th Heart/Vascular Dr Office	Annual	10:06:06 AM	11/23/2022	
Strobe	4th Heart/Vascular Dr Office	Annual	10:06:19 AM	11/23/2022	
Strobe	4th Heart/Vascular Drs Station	Annual	10:00:37 AM	11/23/2022	
Strobe	4th Heart/Vascular Drs Station	Annual	10:05:07 AM	11/23/2022	
Strobe	4th Heart/Vascular Echo Viewing rm	Annual	10:07:21 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:00:55 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:01:56 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:02:12 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:02:20 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:02:27 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:02:33 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:02:40 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:04:27 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:04:33 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:04:38 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:04:45 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:08:01 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:08:12 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:26:36 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:26:44 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:26:51 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:26:55 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:26:59 AM	11/23/2022	
Strobe	4th Heart/Vascular Exam room	Annual	10:27:07 AM	11/23/2022	
Strobe	4th Heart/Vascular Heart Lab	Annual	10:09:45 AM	11/23/2022	
Strobe	4th Heart/Vascular Heart Lab	Annual	10:10:07 AM	11/23/2022	
Strobe	4th Heart/Vascular Heart Lab	Annual	10:10:59 AM	11/23/2022	
Strobe	4th Heart/Vascular Nurses Station	Annual	10:07:56 AM	11/23/2022	
Strobe	4th Heart/Vascular Reception	Annual	10:03:22 AM	11/23/2022	
Strobe	4th Heart/Vascular Restroom	Annual	10:01:03 AM	11/23/2022	
Strobe	4th Heart/Vascular Restroom	Annual	10:08:07 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:12:16 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:12:28 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:18:36 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:27:40 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:28:04 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:28:09 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:28:14 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:28:19 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:28:23 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:28:29 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:28:37 AM	11/23/2022	
Strobe	4th Nuclear Med Exam rm	Annual	10:29:26 AM	11/23/2022	
Strobe	4th Nuclear Med Office	Annual	10:12:47 AM	11/23/2022	
Strobe	4th Nuclear Med Office	Annual	10:13:39 AM	11/23/2022	
Strobe	4th Nuclear Med Office	Annual	10:17:49 AM	11/23/2022	
Strobe	4th Nuclear Med Office	Annual	10:19:27 AM	11/23/2022	
Strobe	4th Nuclear Med Office	Annual	10:22:14 AM	11/23/2022	
Strobe	4th Nuclear Med Office	Annual	10:22:16 AM	11/23/2022	
Strobe	4th Nuclear Med Restroom	Annual	10:17:12 AM	11/23/2022	
Strobe	4th Nuclear Med Restroom	Annual	10:19:42 AM	11/23/2022	
Strobe	4th Nuclear Med Restroom	Annual	10:21:47 AM	11/23/2022	
Strobe	4th Nuclear Med Storage	Annual	10:27:35 AM	11/23/2022	
Strobe	5th Bathroom	Annual	9:20:19 AM	11/23/2022	
Strobe	5th Cardio Suites	Annual	9:18:29 AM	11/23/2022	
Strobe	5th Cardio Suites	Annual	9:18:53 AM	11/23/2022	
Strobe	5th Cardio Suites	Annual	9:20:03 AM	11/23/2022	
Strobe	5th Cardio Suites	Annual	9:21:31 AM	11/23/2022	
Strobe	5th Cardio Suites	Annual	9:23:29 AM	11/23/2022	
Strobe	5th Office	Annual	9:14:22 AM	11/23/2022	
Strobe	5th breakroom	Annual	9:20:26 AM	11/23/2022	
Strobe	5th conference room	Annual	9:19:06 AM	11/23/2022	
Strobe	5th dr Cardio Suites	Annual	9:21:39 AM	11/23/2022	
Strobe	5th nurse station	Annual	9:18:59 AM	11/23/2022	
Strobe	5th office	Annual	9:20:55 AM	11/23/2022	
Strobe	5th Bathroom Cardio Suites	Annual	9:19:52 AM	11/23/2022	
Strobe	5th Conference Room	Annual	9:34:52 AM	11/23/2022	
Strobe	5th Laundry	Annual	9:14:54 AM	11/23/2022	
Strobe	5th Medical records	Annual	9:11:31 AM	11/23/2022	
Strobe	5th Medical records	Annual	9:11:41 AM	11/23/2022	
Strobe	5th Mens Restroom	Annual	9:07:26 AM	11/23/2022	
Strobe	5th PFT Office	Annual	9:35:08 AM	11/23/2022	
Strobe	5th Pulminary Providers Office	Annual	9:12:29 AM	11/23/2022	
Strobe	5th Pulminary Registration Office	Annual	9:12:05 AM	11/23/2022	
Strobe	5th Pulminary Restroom by exam rms	Annual	9:10:04 AM	11/23/2022	
Strobe	5th Pulminary exam rm 1	Annual	9:17:38 AM	11/23/2022	
Strobe	5th Pulminary exam rm 2	Annual	9:10:41 AM	11/23/2022	
Strobe	5th Pulminary exam rm 3	Annual	9:10:33 AM	11/23/2022	
Strobe	5th Pulminary exam rm 4	Annual	9:17:44 AM	11/23/2022	
Strobe	5th Pulminary exam rm 5	Annual	9:10:53 AM	11/23/2022	
Strobe	5th Pulminary exam rm 6	Annual	9:11:07 AM	11/23/2022	
Strobe	5th Pulminary exam rm 7	Annual	9:11:13 AM	11/23/2022	
Strobe	5th Pulminary exam rm 8	Annual	9:11:24 AM	11/23/2022	
Strobe	5th Research Cardio Suites	Annual	9:18:42 AM	11/23/2022	
Strobe	5th Training Rm	Annual	9:35:00 AM	11/23/2022	
Strobe	5th Womens Restroom	Annual	9:07:58 AM	11/23/2022	
Strobe	5th office Cardio Suites	Annual	9:24:00 AM	11/23/2022	
Strobe	5th office Cardio Suites	Annual	9:24:16 AM	11/23/2022	
Strobe	5th EEG Registration	Annual	9:13:30 AM	11/23/2022	
Strobe	5th In Break rm Suite 560	Annual	9:27:23 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:22:18 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:25:55 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:26:18 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:26:27 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:26:52 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:27:02 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:27:11 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:28:24 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:28:29 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:34:12 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:34:29 AM	11/23/2022	
Strobe	5th In Exam rm of Suite 560	Annual	9:34:33 AM	11/23/2022	
Strobe	5th In Office Suite 560	Annual	9:21:53 AM	11/23/2022	
Strobe	5th In Office Suite 560	Annual	9:26:07 AM	11/23/2022	
Strobe	5th In Office Suite 560	Annual	9:26:39 AM	11/23/2022	
Strobe	5th In Restroom Suite 560	Annual	9:21:59 AM	11/23/2022	
Strobe	5th In Restroom Suite 560	Annual	9:25:12 AM	11/23/2022	
Strobe	5th In Restroom Suite 560	Annual	9:27:44 AM	11/23/2022	
Strobe	5th In Storage rm of Suite 560	Annual	9:28:35 AM	11/23/2022	
Strobe	5th Pulminary Restroom	Annual	9:12:40 AM	11/23/2022	
Strobe	5th Pulminary Business Office	Annual	9:12:45 AM	11/23/2022	
Strobe	5th Pulminary Corridor	Annual	9:10:59 AM	11/23/2022	
Strobe	5th Pulminary Dr Office 2	Annual	9:13:00 AM	11/23/2022	
Strobe	5th Pulminary in break rm	Annual	9:13:11 AM	11/23/2022	
Strobe	5th Sleep Center Bathroom	Annual	9:13:21 AM	11/23/2022	
Strobe	5th Sleep Center Bathroom	Annual	9:15:26 AM	11/23/2022	
Strobe	5th Sleep Center Bathroom	Annual	9:15:44 AM	11/23/2022	
Strobe	5th Sleep Center Bathroom	Annual	9:16:14 AM	11/23/2022	
Strobe	5th Sleep Center Bathroom	Annual	9:16:33 AM	11/23/2022	
Strobe	5th Sleep Center Bedroom	Annual	9:15:20 AM	11/23/2022	
Strobe	5th Sleep Center Bedroom	Annual	9:15:38 AM	11/23/2022	
Strobe	5th Sleep Center Bedroom	Annual	9:16:08 AM	11/23/2022	
Strobe	5th Sleep Center Bedroom	Annual	9:16:26 AM	11/23/2022	
Strobe	5th Sleep Center Bedroom	Annual	9:17:16 AM	11/23/2022	
Strobe	5th Sleep Center Conference	Annual	9:17:00 AM	11/23/2022	
Strobe	5th Sleep Center Pt lounge	Annual	9:16:46 AM	11/23/2022	
Strobe	5th Sleep Center monitor rm	Annual	9:15:01 AM	11/23/2022	
Strobe	5th Sleep Center monitor rm	Annual	9:15:08 AM	11/23/2022	
Strobe	5th Sleep Center office	Annual	9:13:42 AM	11/23/2022	
Strobe	5th Sleep Center office	Annual	9:14:03 AM	11/23/2022	
Initiating	
Duct Detector	2nd Mechanical AHU 3 Return	Annual	11:14:52 AM	11/28/2022	
Duct Detector	2nd Mechanical AHU 3 Supply	Annual	11:18:52 AM	11/28/2022	
Duct Detector	2nd Mechanical AHU 4 Return	Annual	11:21:56 AM	11/28/2022	
Duct Detector	2nd Mechanical AHU 4 Supply	Annual	11:19:05 AM	11/28/2022	
Duct Detector	Penthouse AHU 5 Return	Annual	8:53:54 AM	11/23/2022	
Duct Detector	Penthouse AHU 5 Supply	Annual	8:59:55 AM	11/23/2022	
Duct Detector	Penthouse AHU 6 Return	Annual	8:59:53 AM	11/23/2022	
Duct Detector	Penthouse AHU-6 Supply	Annual	8:55:34 AM	11/23/2022	
Heat Detector	Basement Vault tag on strobe	Annual	4:01:11 PM	11/22/2022	
Heat Detector	Basement Vault Break rm tag on strobe	Annual	4:00:41 PM	11/22/2022	
Heat Detector	Basement Inside Electrical Outside Entrance tag on strobe	Annual	10:51:33 AM	11/28/2022	
Heat Detector	2nd Mechanical rm tag on Duct Detector	Annual	11:14:49 AM	11/28/2022	
Heat Detector	3rd Suite 340 Mechanical tag in door	Annual	12:06:58 PM	11/23/2022	
Heat Detector	Penthouse tag on Speaker/Strobe	Annual	8:52:14 AM	11/23/2022	
Heat Detector	Penthouse tag on Speaker/Strobe	Annual	8:52:16 AM	11/23/2022	
Heat Detector	Penthouse Boiler rm tag in door	Annual	8:50:46 AM	11/23/2022	
Heat Detector	Penthouse Elevator rm	Annual	8:49:33 AM	11/23/2022	
Heat Detector	Penthouse Elevator rm	Annual	8:53:35 AM	11/23/2022	
Heat Detector	Penthouse Storage rm in Boiler rm tag in door	Annual	8:50:24 AM	11/23/2022	
Pull Station	Basement Corridor	Annual	9:15:30 AM	11/28/2022	
Pull Station	Basement Corridor	Annual	9:21:48 AM	11/28/2022	
Pull Station	Basement Corridor	Annual	9:30:20 AM	11/28/2022	
Pull Station	Basement Corridor to Hospital	Annual	11:32:28 AM	11/28/2022	
Pull Station	Basement Media Center by Stair D	Annual	9:16:22 AM	11/28/2022	
Pull Station	Basement APOGEE	Annual	11:32:10 AM	11/28/2022	
Pull Station	Basement Corridor by Digestive Health	Annual	9:40:54 AM	11/28/2022	
Pull Station	Basement Electrical rm Outside Entrance	Annual	10:51:41 AM	11/28/2022	
Pull Station	Basement vault	Annual	11:32:33 AM	11/28/2022	
Pull Station	Basement Digestive Health Corridor	Annual	11:32:18 AM	11/28/2022	
Pull Station	Basement Digestive Health Corridor by Stairwell C	Annual	11:32:22 AM	11/28/2022	
Pull Station	Basement Inside Electrical rm Outside Entrance	Annual	10:52:22 AM	11/28/2022	
Pull Station	Basement Lab Corridor Stairwell	Annual	9:22:29 AM	11/28/2022	
Pull Station	Basement Plant Engineering Corridor	Annual	11:32:14 AM	11/28/2022	
Pull Station	1st Corridor beside Stairway A	Annual	11:40:40 AM	11/28/2022	
Pull Station	1st Corridor infectious disease	Annual	11:33:15 AM	11/28/2022	
Pull Station	1st Corridor infectious disease	Annual	11:33:19 AM	11/28/2022	
Pull Station	1st Corridor to Hospital	Annual	11:33:08 AM	11/28/2022	
Pull Station	1st Corridor to Hospital	Annual	11:33:11 AM	11/28/2022	
Pull Station	1st Corridor to Hospital	Annual	11:33:25 AM	11/28/2022	
Pull Station	1st Corridor by Neuroscience Suite 125	Annual	11:24:43 AM	11/28/2022	
Pull Station	1st Corridor in Neuroscience Suite 125	Annual	11:31:28 AM	11/28/2022	
Pull Station	1st Diabetes Corridor	Annual	11:32:54 AM	11/28/2022	
Pull Station	1st Diabetes Corridor	Annual	11:33:00 AM	11/28/2022	
Pull Station	1st Hyperbaric Wound Center Exam rm	Annual	11:41:30 AM	11/28/2022	
Pull Station	1st Infusion Center Corridor	Annual	11:40:56 AM	11/28/2022	
Pull Station	1st Infusion Center Corridor	Annual	11:41:02 AM	11/28/2022	
Pull Station	1st Oncology Corridor	Annual	9:47:19 AM	11/28/2022	
Pull Station	1st Oncology Corridor	Annual	11:32:43 AM	11/28/2022	
Pull Station	1st Oncology Corridor	Annual	11:32:48 AM	11/28/2022	
Pull Station	1st Oncology Entrance	Annual	11:32:38 AM	11/28/2022	
Pull Station	1st Performance Improvement Corridor	Annual	11:33:29 AM	11/28/2022	
Pull Station	1st Performance Improvement Corridor	Annual	11:33:37 AM	11/28/2022	
Pull Station	1st Staff Elevator Lobby	Annual	11:33:48 AM	11/28/2022	
Pull Station	1st Suite 190 Corridor	Annual	11:33:04 AM	11/28/2022	
Pull Station	2nd Corridor by Pharmacy	Annual	11:10:02 AM	11/28/2022	
Pull Station	2nd Corridor by Stairwell B	Annual	11:11:44 AM	11/28/2022	
Pull Station	2nd Corridor by Suite 250	Annual	11:41:17 AM	11/28/2022	
Pull Station	2nd Corridor to Hospital	Annual	11:41:26 AM	11/28/2022	
Pull Station	2nd Mechanical rm	Annual	11:13:52 AM	11/28/2022	
Pull Station	2nd Mechanical rm	Annual	11:41:13 AM	11/28/2022	
Pull Station	2nd OB-GYN Corridor	Annual	11:41:09 AM	11/28/2022	
Pull Station	2nd ENT Corridor	Annual	11:41:21 AM	11/28/2022	
Pull Station	2nd Employee Staff Corridor	Annual	11:13:23 AM	11/28/2022	
Pull Station	2nd Front Lobby	Annual	11:07:54 AM	11/28/2022	
Pull Station	3rd Corridor by Internal Med	Annual	12:08:22 PM	11/23/2022	
Pull Station	3rd Corridor by Stairwell A	Annual	11:50:46 AM	11/23/2022	
Pull Station	3rd Corridor to Hospital	Annual	12:01:04 PM	11/23/2022	
Pull Station	3rd Employee Staff Corridor	Annual	11:49:39 AM	11/23/2022	
Pull Station	3rd Internal Med Corridor by Exam 21	Annual	11:58:08 AM	11/23/2022	
Pull Station	3rd Internal Med Corridor by Stair B	Annual	11:54:36 AM	11/23/2022	
Pull Station	3rd Internal Med Corridor by nurse station	Annual	11:52:08 AM	11/23/2022	
Pull Station	3rd Nephrology Suite 330 Corridor	Annual	12:04:03 PM	11/23/2022	
Pull Station	3rd Nephrology Suite 330 Corridor by Stair C	Annual	12:02:57 PM	11/23/2022	
Pull Station	3rd Suite 340 Corridor	Annual	12:05:40 PM	11/23/2022	
Pull Station	3rd Suite 340 Procedure rm	Annual	12:07:07 PM	11/23/2022	
Pull Station	4th Corridor by Heart/Vascular Registration	Annual	9:57:21 AM	11/23/2022	
Pull Station	4th Corridor by Nuclear Med Waiting rm	Annual	10:20:54 AM	11/23/2022	
Pull Station	4th Corridor by Stairwell A	Annual	9:58:28 AM	11/23/2022	
Pull Station	4th Corridor to Hospital	Annual	10:11:48 AM	11/23/2022	
Pull Station	4th Waiting Area for Heart/Vascular Registration	Annual	10:00:04 AM	11/23/2022	
Pull Station	4th Employee Staff Corridor	Annual	9:56:52 AM	11/23/2022	
Pull Station	4th Heart/Vascular Corridor	Annual	10:01:22 AM	11/23/2022	
Pull Station	4th Heart/Vascular Corridor	Annual	10:03:04 AM	11/23/2022	
Pull Station	4th Nuclear Med Corridor	Annual	10:17:22 AM	11/23/2022	
Pull Station	4th Nuclear Med Corridor	Annual	10:18:23 AM	11/23/2022	
Pull Station	4th Nuclear Med Corridor	Annual	10:29:11 AM	11/23/2022	
Pull Station	5th Corridor Suite 560	Annual	9:22:42 AM	11/23/2022	
Pull Station	5th Corridor by Suite 560	Annual	9:29:50 AM	11/23/2022	
Pull Station	5th Corridor by office	Annual	9:21:16 AM	11/23/2022	
Pull Station	5th Corridor by stairwell c	Annual	9:19:42 AM	11/23/2022	
Pull Station	5th Corridor to Hospital	Annual	9:18:11 AM	11/23/2022	
Pull Station	5th Stairwell A	Annual	9:08:15 AM	11/23/2022	
Pull Station	5th Stairwell B	Annual	9:10:12 AM	11/23/2022	
Pull Station	5th Employee Staff Corridor	Annual	9:07:00 AM	11/23/2022	
Pull Station	5th Pulminary Corridor	Annual	9:09:36 AM	11/23/2022	
Pull Station	5th Pulminary Lobby	Annual	9:08:53 AM	11/23/2022	
Pull Station	5th Sleep room Storage	Annual	9:14:41 AM	11/23/2022	
Pull Station	Penthouse	Annual	8:52:32 AM	11/23/2022	
Pull Station	Penthouse Top of Stair	Annual	8:48:50 AM	11/23/2022	
Smoke Detector	Basement Corridor by Suite M20	Sensitivity Tested	9:33:20 AM	11/28/2022	
Smoke Detector	Basement Corridor by Suite M20	Sensitivity Tested	9:34:34 AM	11/28/2022	
Smoke Detector	Basement Curtain smoke	Sensitivity Tested	9:28:20 AM	11/28/2022	
Smoke Detector	Basement Library training room	Sensitivity Tested	9:21:12 AM	11/28/2022	
Smoke Detector	Basement Media Center by Stair D	Sensitivity Tested	9:21:16 AM	11/28/2022	
Smoke Detector	Basement Media Center by Stair D West	Sensitivity Tested	9:21:20 AM	11/28/2022	
Smoke Detector	Basement Public Elevator Foyer	Sensitivity Tested	9:27:58 AM	11/28/2022	
Smoke Detector	Basement Above Fire Panel	Sensitivity Tested	9:13:09 AM	11/28/2022	
Smoke Detector	Basement Beside Stair	Sensitivity Tested	9:17:07 AM	11/28/2022	
Smoke Detector	Basement Inside Family Medicine MH647 Storage	Sensitivity Tested	12:06:15 PM	11/28/2022	
Smoke Detector	Basement Inside Telephone rm by Hospital Corridor	Sensitivity Tested	9:41:55 AM	11/28/2022	
Smoke Detector	Basement Staff Elevator M	Sensitivity Tested	9:26:33 AM	11/28/2022	
Smoke Detector	1st Electrical Closet by Neuroscience Suite 125	Sensitivity Tested	10:20:49 AM	11/28/2022	
Smoke Detector	1st Electrical rm above Transponder	Sensitivity Tested	10:17:42 AM	11/28/2022	
Smoke Detector	1st Diabetes Corridor	Sensitivity Tested	10:17:51 AM	11/28/2022	
Smoke Detector	1st Diabetes Nurses Station	Sensitivity Tested	10:17:47 AM	11/28/2022	
Smoke Detector	1st Diabetes Waiting rm	Sensitivity Tested	10:17:56 AM	11/28/2022	
Smoke Detector	1st Oncology Corridor Entry	Sensitivity Tested	10:04:49 AM	11/28/2022	
Smoke Detector	1st Oncology Office	Sensitivity Tested	10:04:17 AM	11/28/2022	
Smoke Detector	1st Oncology Register	Sensitivity Tested	10:04:35 AM	11/28/2022	
Smoke Detector	1st Oncology Waiting rm	Sensitivity Tested	10:04:07 AM	11/28/2022	
Smoke Detector	1st Public Elevator Lobby	Sensitivity Tested	10:17:37 AM	11/28/2022	
Smoke Detector	1st Staff Elevator Lobby	Sensitivity Tested	10:03:47 AM	11/28/2022	
Smoke Detector	2nd Elevator Lobby	Sensitivity Tested	10:59:01 AM	11/28/2022	
Smoke Detector	2nd In Electrical rm above Transponder	Sensitivity Tested	11:05:47 AM	11/28/2022	
Smoke Detector	2nd In Optical office	Sensitivity Tested	10:56:37 AM	11/28/2022	
Smoke Detector	2nd In Optical office	Sensitivity Tested	10:59:28 AM	11/28/2022	
Smoke Detector	2nd Main Hallway South	Sensitivity Tested	11:02:37 AM	11/28/2022	
Smoke Detector	2nd Staff Elevator Lobby	Sensitivity Tested	11:03:45 AM	11/28/2022	
Smoke Detector	3rd Elevator Lobby	Sensitivity Tested	12:21:28 PM	11/23/2022	
Smoke Detector	3rd Employee Staff Corridor	Sensitivity Tested	12:19:01 PM	11/23/2022	
Smoke Detector	3rd In Electrical rm Internal Med	Sensitivity Tested	12:21:58 PM	11/23/2022	
Smoke Detector	3rd In Electrical rm above Transponder	Sensitivity Tested	12:24:00 PM	11/23/2022	
Smoke Detector	4th Elevator Lobby	Sensitivity Tested	10:38:24 AM	11/23/2022	
Smoke Detector	4th Employee Staff Corridor	Sensitivity Tested	10:35:33 AM	11/23/2022	
Smoke Detector	4th In Electrical rm above Transponder	Sensitivity Tested	10:38:33 AM	11/23/2022	
Smoke Detector	5th Electrical rm 5112	Sensitivity Tested	9:37:40 AM	11/23/2022	
Smoke Detector	5th Elevator Lobby	Sensitivity Tested	9:36:33 AM	11/23/2022	
Smoke Detector	5th Employee Staff Corridor	Sensitivity Tested	9:53:56 AM	11/23/2022	
Waterflow Switch	Basement Inside Corridor Vault	Annual	3:14:09 PM	11/22/2022	
Waterflow Switch	Basement Inside Stairwell A	Annual	3:13:18 PM	11/22/2022	
Waterflow Switch	1st Inside Stairwell B	Annual	3:13:23 PM	11/22/2022	
Waterflow Switch	2nd Inside Stairwell B	Annual	3:13:32 PM	11/22/2022	
Waterflow Switch	2nd Inside Stairwell C	Annual	3:13:42 PM	11/22/2022	
Waterflow Switch	3rd Above Ceiling Stairwell C	Annual	3:13:47 PM	11/22/2022	
Waterflow Switch	3rd Inside Stairwell B	Annual	3:13:37 PM	11/22/2022	
Waterflow Switch	4th Above Ceiling Stairwell B	Annual	3:13:14 PM	11/22/2022	
Waterflow Switch	4th Above Ceiling Stairwell C	Annual	3:13:54 PM	11/22/2022	
Waterflow Switch	5th Above Ceiling Stairwell B	Annual	3:13:09 PM	11/22/2022	
Waterflow Switch	5th Above Ceiling Stairwell C	Annual	3:14:04 PM	11/22/2022	
Waterflow Switch	Penthouse	Annual	3:13:59 PM	11/22/2022	
Monitor	
Monitoring	Basement FACP Alarm Monitoring	Annual	9:27:39 AM	11/21/2022	
Monitoring	Basement FACP Supervisory Monitoring	Annual	9:27:59 AM	11/21/2022	
Monitoring	Basement FACP Trouble  Monitoring	Annual	9:34:37 AM	11/21/2022	
Supervisory	
Tamper Switch	Basement Above Ceiling Corridor by Stairwell A	Annual	3:14:51 PM	11/22/2022	
Tamper Switch	Basement Above Ceiling Digestive Health Office area tag on ceiling	Annual	3:14:23 PM	11/22/2022	
Tamper Switch	Basement Above Ceiling Stairwell C	Annual	3:14:56 PM	11/22/2022	
Tamper Switch	Basement Inside Sprinkler rm	Annual	3:16:43 PM	11/22/2022	
Tamper Switch	Basement Inside Sprinkler rm	Annual	3:16:48 PM	11/22/2022	
Tamper Switch	Basement Inside Stairwell A	Annual	3:15:29 PM	11/22/2022	
Tamper Switch	Basement Inside New Urgent Care Suite MH602 tag on ceiling	Annual	1:01:49 PM	11/21/2022	
Tamper Switch	1st Inside Stairwell B	Annual	3:15:40 PM	11/22/2022	
Tamper Switch	2nd Inside Stairwell B	Annual	3:15:56 PM	11/22/2022	
Tamper Switch	3rd Inside Stairwell B	Annual	3:16:01 PM	11/22/2022	
Tamper Switch	3rd Inside Stairwell C	Annual	3:16:10 PM	11/22/2022	
Tamper Switch	3rd Inside Stairwell C	Annual	3:16:18 PM	11/22/2022	
Tamper Switch	4th Above Ceiling Stairwell B	Annual	3:15:14 PM	11/22/2022	
Tamper Switch	4th Above Ceiling Stairwell B	Annual	3:16:25 PM	11/22/2022	
Tamper Switch	5th Above Ceiling Stairwell B	Annual	3:15:07 PM	11/22/2022	
Tamper Switch	5th Above Ceiling Stairwell C	Annual	3:16:37 PM	11/22/2022	
Tamper Switch	Penthouse	Annual	3:14:44 PM	11/22/2022	
Tamper Switch	Penthouse Elevator	Annual	3:16:30 PM	11/22/2022	
Water Pressure Switch	Basement Inside Sprinkler rm	Annual	3:14:16 PM	11/22/2022	

Building: 560 W. Mitchell St MOB	Control Panel: 2  	
The Inspection & Testing section lists all of the items inspected in your building.  Items are grouped by Passed or Failed/Other. Items are listed by Category. Each item includes the services performed, and the time & date at which testing occurred.	

Device Type	Location	Service	Time	Date	
Passed	
Control	
Battery	Basement Inside Electrical rm across from Suite 125	Annual	11:11:46 AM	11/21/2022	
Battery	Basement Inside Family Medicine MH647 Storage	Annual	10:56:07 AM	11/21/2022	
Battery	Basement Inside Family Medicine MH647 Storage	Annual	10:57:44 AM	11/21/2022	
Battery	Basement Inside Fire Panel	Annual	9:37:28 AM	11/21/2022	
Battery	Basement Inside Fire Panel	Annual	9:37:30 AM	11/21/2022	
Battery	1st Inside Electrical rm across from Suite 125	Annual	11:10:09 AM	11/21/2022	
Power Supply	Basement Inside Family Medicine MH647 Storage	Annual	10:55:06 AM	11/21/2022	

Service Summary	
Generated by: BuildingReports.com	
Building: 560 W. Mitchell St MOB	
The Service Summary section provides an overview of the services performed in this report.	

Device Type	Service	Quantity	
Passed	
Annunciator	Annual	1	
Battery	Annual	19	
Battery	Replaced	2	
Communicator	Annual	1	
Control Panel	Annual	1	
Duct Detector	Annual	8	
Expander Panel	Annual	5	
Heat Detector	Annual	11	
Monitoring	Annual	3	
Power Supply	Annual	3	
Pull Station	Annual	80	
Releasing Device	Annual	6	
Smoke Detector	Sensitivity Tested	39	
Speaker/Strobe	Annual	161	
Speaker/Strobe	Repaired	3	
Speaker	Annual	45	
Strobe	Annual	529	
Tamper Switch	Annual	18	
Water Pressure Switch	Annual	1	
Waterflow Switch	Annual	12	
Total	948	
Grand Total	948	

Auxiliary Functions Testing	
Generated by: BuildingReports.com	

Building: 560 W. Mitchell St MOB	Control Panel: 1 - Johnson Controls 3030	
The Auxiliary Functions Testing section lists each of the ancillary items, systems, and emergency equipment that are controlled by the system control unit. Items are grouped by Passed or Failed/Other. The items are listed by device type, and a check box is provided to indicate if the test conducted was simulated.	
Type	Location	Comment	ScanID	Simulated	
Passed	
Releasing Device	
Door Holder	Basement Corridor by Suite M20	Passed	20458175	¨	
Door Holder	Basement Corridor by Suite M20	Passed	20458176	¨	
Door Holder	1st Entrance from halfway to Oncology	Passed	20458292	¨	
Door Holder	1st Oncology Corridor	Passed	20458246	¨	
Door Holder	1st Oncology Corridor	Passed	36899135	¨	
Door Holder	2nd Corridor OB-GYN	Passed	20458482	¨	
Smoke Detector	
Door Release	Basement Curtain smoke	Passed	65661852		
Door Release	Basement Public Elevator Foyer	Passed	36899138		

Sensitivity Testing	
Generated by: BuildingReports.com	

Building: 560 W. Mitchell St MOB	Control Panel: 1 - Johnson Controls 3030	
The Sensitivity Testing section details the sensitivity test ranges and acceptable readings for each type of device.  Items are grouped by Passed or Failed/Other. Normally, Devices that perform outside the acceptable range of sensitivity are listed in Failed/Other.	
Location	Address	Model #	Range	Value	ScanID	
Passed	
Smoke Detector	
Basement Corridor by Suite M20	1-3 14	2351J	0.5 - 2.35	1.87	20458177	
Basement Corridor by Suite M20	1-3 15	2351J	0.5 - 2.35	1.88	20458174	
Basement Curtain smoke	1-3 33	2951J	0.5 - 3.0	2.5	65661852	
Basement Library training room	1-3 17	2951J	0.5 - 3.0	2.23	20458120	
Basement Media Center by Stair D	1-3 18	2351J	0.5 - 2.35	1.51	20458126	
Basement Media Center by Stair D West	1-3 19	2351J	0.5 - 2.35	1.43	20458129	
Basement Public Elevator Foyer	1-3 22	2951J	0.5 - 3.0	2.5	36899138	
Basement Above Fire Panel	1-3 16	2951J	0.5 - 3.0	2.34	36899125	
Basement Beside Stair	1-3 24	2351J	0.5 - 2.35	1.65	20458142	
Basement Inside Family Medicine MH647 Storage	1-3 34	2951J	0.5 - 3.0	1.65	29108019	
Basement Inside Telephone rm by Hospital Corridor	1-3 13	2351J	0.5 - 2.35	1.67	20458211	
Basement Staff Elevator M	1-3 23	2351J	0.5 - 2.35	1.68	20458213	
1st Electrical Closet by Neuroscience Suite 125	1-3 32	2351J	0.5 - 2.35	1.07	23202108	
1st Electrical rm above Transponder	1-3 01	2351J	0.5 - 2.35	2.07	20458374	
1st Diabetes Corridor	1-3 02	2551J	0.97 - 2.29	2.12	20458314	
1st Diabetes Nurses Station	1-3 03	2551J	0.97 - 2.29	1.83	20458317	
1st Diabetes Waiting rm	1-3 08	2551J	0.97 - 2.29	1.79	20458294	
1st Oncology Corridor Entry	1-3 04	2351J	0.5 - 2.35	1.87	20458245	
1st Oncology Office	1-3 07	2551J	0.97 - 2.29	2.02	20458273	
1st Oncology Register	1-3 05	2551J	0.97 - 2.29	1.95	20458247	
1st Oncology Waiting rm	1-3 06	2551J	0.97 - 2.29	1.83	20458277	
1st Public Elevator Lobby	1-3 11	2951J	0.5 - 3.0	2.25	20458440	
1st Staff Elevator Lobby	1-3 09	2351J	0.51 - 2.35	1.88	20458430	
2nd Elevator Lobby	1-1 22	2551J	0.97 - 2.29	2.01	20458460	
2nd In Electrical rm above Transponder	1-1 25	2351J	0.5 - 2.35	1.38	20458571	
2nd In Optical office	1-1 24	2351J	0.5 - 2.35	2.12	20458479	
2nd In Optical office	1-027	2551J	0.97 - 2.29	2.12	20458526	
2nd Main Hallway South	1-1 26	2551J	0.97 - 2.29	2.18	47161099	
2nd Staff Elevator Lobby	1-1 21	2951J	0.5 - 3.0	2.25	38839325	
3rd Elevator Lobby	1-1 13	2551J	0.97 - 2.29	1.03	20458587	
3rd Employee Staff Corridor	1-1 12	2551J	0.97 - 2.29	1.14	20458577	
3rd In Electrical rm Internal Med	1-1 14	2351J	0.5 - 2.35	1.44	20458595	
3rd In Electrical rm above Transponder	1-1 10	2551J	0.97 - 2.29	1.92	20458689	
4th Elevator Lobby	1-2 11	2951J	0.5 - 3.0	1.98	20458829	
4th Employee Staff Corridor	1-2 12	2351J	0.5 - 2.35	1.3	20458822	
4th In Electrical rm above Transponder	1-2 15	2351J	0.5 - 2.35	1.64	20458896	
5th Electrical rm 5112	1-2 16	2351J	0.5 - 2.35	1.32	20459011	
5th Elevator Lobby	1-2 13	2551J	0.97 - 2.29	1.01	20458946	
5th Employee Staff Corridor	1-2 14	2551J	0.97 - 2.29	2.1	20458940	
Device Total: 39	

Smoke Management Testing
Generated by: BuildingReports.com

Building: 560 W. Mitchell St MOB	Control Panel: 1 - Johnson Controls  3030	
The Smoke Management Testing section details the test and inspection of device items that are involved in controlling the spread of smoke in a building. Items are grouped by Passed or Failed/ Other.	
`  Location	Description	?  Comment	ScanID	Simulated	
Passed	
Releasing Device	
Basement Corridor by Suite M20	Door Holder	Passed	20458175	¨	
Basement Corridor by Suite M20	Door Holder	Passed	20458176	¨	
1st Entrance from halfway to Oncology	Door Holder	Passed	20458292	¨	
1st Oncology Corridor	Door Holder	Passed	20458246	¨	
1st Oncology Corridor	Door Holder	Passed	36899135	¨	
2nd Corridor OB-GYN	Door Holder	Passed	20458482	¨	

Battery & Power Supply Testing
Generated by: BuildingReports.com

Building: 560 W. Mitchell St MOB	Control Panel: 1 - Johnson Controls 3030	
The Battery & Power Supply Testing section details the readings and measurements of batteries and power supplies used to provide power to the fire alarm and life safety systems. Items are grouped by Passed or Failed/Other.	
Battery	
Type	Location	Rated Ah	Rated Volts	Pre Test	Post Test	Min Ah	Tested Ah	
Passed	
Sealed Lead Acid	Basement Dialer Above FACP	5	12	12.56	12.56	3.25	3.6	
Sealed Lead Acid	1st Inside Transponder Panel Electrical rm	55	12	13.37	13.25	35.75	38	
Sealed Lead Acid	1st Inside Transponder Panel Electrical rm	55	12	13.46	13.34	35.75	48	
Sealed Lead Acid	2nd Front Lobby in Annunciator panel	26	12	13.26	13.07	16.9	17	
Sealed Lead Acid	2nd Front Lobby in Annunciator panel	26	12	13.22	13.03	16.9	18	
Sealed Lead Acid	2nd Inside Transponder Panel Electrical rm	26	12	new				
Sealed Lead Acid	2nd Inside Transponder Panel Electrical rm	26	12	new				
Sealed Lead Acid	3rd Inside Transponder Panel Electrical rm	55	12	13.47	13.35	35.75	38	
Sealed Lead Acid	3rd Inside Transponder Panel Electrical rm	55	12	13.44	13.32	35.75	38	
Sealed Lead Acid	3rd Internal Med South Electrical rm	7	12	12.88	12.69	4.55	7.8	
Sealed Lead Acid	3rd Internal Med South Electrical rm	7	12	12.87	12.71	4.55	7.8	
Sealed Lead Acid	4th Inside Transponder Panel Electrical	26	12	13.35	13.12	16.9	17	
Sealed Lead Acid	4th Inside Transponder Panel Electrical	26	12	13.26	12.97	16.9	17	
Sealed Lead Acid	5th Inside Transponder Panel Electrical rm 5112	55	12	13.63	13.51	35.75	44	
Sealed Lead Acid	5th Inside Transponder Panel Electrical rm 5112	55	12	13.68	13.51	35.75	40	
Building: 560 W. Mitchell St MOB	Control Panel: 2	
The Battery & Power Supply Testing section details the readings and measurements of batteries and power supplies used to provide power to the fire alarm and life safety systems. Items are grouped by Passed or Failed/Other.	
Battery	
Type	Location	Rated Ah	Rated Volts	Pre Test	Post Test	Min Ah	Tested Ah	
Passed	
Sealed Lead Acid	Basement Inside Electrical rm across from Suite 125	7	12	12.82	12.65	4.55	7.8	
Sealed Lead Acid	Basement Inside Family Medicine MH647 Storage	7	12	12.72	12.59	4.55	7.8	
Sealed Lead Acid	Basement Inside Family Medicine MH647 Storage	7	12	12.71	12.59	4.55	7.6	
Sealed Lead Acid	Basement Inside Fire Panel	26	12	13.16	12.96	16.9	30	
Sealed Lead Acid	Basement Inside Fire Panel	26	12	13.16	12.94	16.9	29	
Sealed Lead Acid	1st Inside Electrical rm across from Suite 125	7	12	12.78	12.60	4.55	7.8	

Inventory & Warranty Report	
Generated by: BuildingReports.com	
Building: 560 W. Mitchell St MOB	Control Panel: 1 - Johnson Controls 3030	
The Inventory & Warranty Report lists each of the devices and items that are included in your Inspection Report. A complete inventory count by device type and category is provided. Items installed within the last 90 days, within the last year, and devices installed for two years or more are grouped together for easy reference.	

Device or Type	Category	% of Inventory	Quantity	
Annunciator	Control	0.11%	1	
Battery	Control	2.22%	21	
Communicator	Control	0.11%	1	
Control Panel	Control	0.11%	1	
Duct Detector	Initiating	0.84%	8	
Expander Panel	Control	0.53%	5	
Heat Detector	Initiating	1.16%	11	
Monitoring	Monitor	0.32%	3	
Power Supply	Control	0.32%	3	
Pull Station	Initiating	8.44%	80	
Releasing Device	Auxiliary	0.63%	6	
Smoke Detector	Initiating	4.11%	39	
Speaker	Indicating	4.75%	45	
Speaker/Strobe	Indicating	17.30%	164	
Strobe	Indicating	55.80%	529	
Tamper Switch	Supervisory	1.90%	18	
Water Pressure Switch	Supervisory	0.11%	1	
Waterflow Switch	Initiating	1.27%	12	

Type	Qty	Model #	Description	Install Date	
New (under 90 days)	
Universal	
Battery	2	PS-12260	Sealed Lead Acid	11/22/2022	
In Service - 1 Year to 2 Years	
Power-Sonic	
Battery	1	PS1250	Sealed Lead Acid	11/03/2021	
PowerRite	
Battery	2	PR12550	Sealed Lead Acid	11/03/2021	
Battery	2	PR1270	Sealed Lead Acid	11/03/2021	
Battery	2	PS-12260	Sealed Lead Acid	11/03/2021	
Wheelock	
Speaker/Strobe	24	ET90-24MCC		08/28/2021	
Strobe	7	STC		08/28/2021	
Johnson Controls	
Smoke Detector	2	2951J	Photoelectric	05/28/2021	
Victaulic	
Tamper Switch	1			05/28/2021	
Wheelock	
Speaker	3	SER		05/28/2021	
In Service - 2 Years to 3 Years	
Universal Battery	
Battery	4	UB12550 AGM	Sealed Lead Acid	12/10/2020	
Wheelock	
Strobe	1	RSS-24MCW		10/02/2020	
In Service - 3 Years to 5 Years	
Power Patrol	
Battery	1	PS-12260	Sealed Lead Acid	09/26/2019	
Power-Sonic	
Battery	1	PS-12260	Sealed Lead Acid	09/26/2019	
Siemens	
Speaker	2	SER		05/28/2018	
System Sensor	
Strobe	5	SRL		05/28/2018	
In Service - 5 Years to 10 Years	
Honeywell	
Power Supply	1	5495		09/28/2015	
Johnson Controls	
Annunciator	1	DR-C3		09/28/2015	
Control Panel	1	3030		09/28/2015	
Expander Panel	5	DR-C3		09/28/2015	
Notifier	
Power Supply	1	FCPS-24S6		09/28/2015	
	
Releasing Device	1		Door Holder	05/28/2015	
Tamper Switch	3	Butterfly		05/28/2015	
Tamper Switch	4	OS&Y		05/28/2015	
Water Pressure Switch	1	OS&Y	Low	05/28/2015	
American	
Tamper Switch	4	Butterfly Valve		05/28/2015	
Johnson Controls	
Duct Detector	6	255-1J	Photoelectric	05/28/2015	
Duct Detector	2	DNR	Photoelectric	05/28/2015	
Heat Detector	11	5551J	Fixed Temperature	05/28/2015	
Pull Station	50	BGX-101L	Dual Action	05/28/2015	
Pull Station	29	JBG-12LX	Dual Action	05/28/2015	
Releasing Device	5		Door Holder	05/28/2015	
Smoke Detector	17	2351J	Photoelectric	05/28/2015	
Smoke Detector	14	2551J	Photoelectric	05/28/2015	
Smoke Detector	6	2951J	Photoelectric	05/28/2015	
Milwaukee	
Tamper Switch	4	Ball Valve		05/28/2015	
Potter Electric	
Waterflow Switch	4	VSR-F		05/28/2015	
System Sensor	
Tamper Switch	1			05/28/2015	
Tamper Switch	1	BB-SC80		05/28/2015	
Waterflow Switch	8	WFD-25		05/28/2015	
Teleguard	
Communicator	1	TG-7	Cellular	05/28/2015	
Monitoring	1		Alarm	05/28/2015	
Monitoring	1		Supervisory	05/28/2015	
Monitoring	1		Trouble	05/28/2015	
Wheelock	
Speaker	40	P82051		05/28/2015	
Speaker/Strobe	1			05/28/2015	
Speaker/Strobe	139	ET70-24MCW		05/28/2015	
Strobe	170			05/28/2015	
Strobe	346	RSS-24MCW		05/28/2015	
In Service - 25 Years or Older	
Johnson Controls	
Pull Station	1	BGX-101L	Dual Action	01/28/1995	
Building: 560 W. Mitchell St MOB	Control Panel: 2	
The Inventory & Warranty Report lists each of the devices and items that are included in your Inspection Report. A complete inventory count by device type and category is provided. Items installed within the last 90 days, within the last year, and devices installed for two years or more are grouped together for easy reference.	
Type	Qty	Model #	Description	Install Date	
In Service - 1 Year to 2 Years	
Oracle	
Battery	2	PS1270	Sealed Lead Acid	11/03/2021	
In Service - 3 Years to 5 Years	
Power-Sonic	
Battery	2	PS-12260	Sealed Lead Acid	09/26/2019	
Battery	2	PS1270	Sealed Lead Acid	09/26/2019	
In Service - 5 Years to 10 Years	
Johnson Controls	
Power Supply	1	3030		09/28/2015	

Zone Address Report
Generated by: BuildingReports.com

Building: 560 W. Mitchell St MOB	Control Panel: 1 - Johnson Controls  3030	
The Zone Address Report lists all of the devices and items that have an individual address, or are grouped together under a common zone.  The device type, location, and description are included for your reference.	
Address	Device Type	Location	Type	ScanID	
Zone/Circuit: 1	
10	Smoke Detector	3rd In Electrical rm above Transponder	Photoelectric	20458689	
12	Smoke Detector	3rd Employee Staff Corridor	Photoelectric	20458577	
13	Smoke Detector	3rd Elevator Lobby	Photoelectric	20458587	
14	Smoke Detector	3rd In Electrical rm Internal Med	Photoelectric	20458595	
19	Duct Detector	2nd Mechanical AHU 4 Return	Photoelectric	20458535	
20	Duct Detector	2nd Mechanical AHU 4 Supply	Photoelectric	20458534	
21	Smoke Detector	2nd Staff Elevator Lobby	Photoelectric	38839325	
22	Smoke Detector	2nd Elevator Lobby	Photoelectric	20458460	
24	Smoke Detector	2nd In Optical office	Photoelectric	20458479	
25	Smoke Detector	2nd In Electrical rm above Transponder	Photoelectric	20458571	
26	Smoke Detector	2nd Main Hallway South	Photoelectric	47161099	
Zone/Circuit: 2	
11	Smoke Detector	4th Elevator Lobby	Photoelectric	20458829	
12	Smoke Detector	4th Employee Staff Corridor	Photoelectric	20458822	
13	Smoke Detector	5th Elevator Lobby	Photoelectric	20458946	
14	Smoke Detector	5th Employee Staff Corridor	Photoelectric	20458940	
15	Smoke Detector	4th In Electrical rm above Transponder	Photoelectric	20458896	
16	Smoke Detector	5th Electrical rm 5112	Photoelectric	20459011	
Zone/Circuit: 3	
01	Smoke Detector	1st Electrical rm above Transponder	Photoelectric	20458374	
02	Smoke Detector	1st Diabetes Corridor	Photoelectric	20458314	
03	Smoke Detector	1st Diabetes Nurses Station	Photoelectric	20458317	
04	Smoke Detector	1st Oncology Corridor Entry	Photoelectric	20458245	
05	Smoke Detector	1st Oncology Register	Photoelectric	20458247	
06	Smoke Detector	1st Oncology Waiting rm	Photoelectric	20458277	
07	Smoke Detector	1st Oncology Office	Photoelectric	20458273	
08	Smoke Detector	1st Diabetes Waiting rm	Photoelectric	20458294	
09	Smoke Detector	1st Staff Elevator Lobby	Photoelectric	20458430	
11	Smoke Detector	1st Public Elevator Lobby	Photoelectric	20458440	
13	Smoke Detector	Basement Inside Telephone rm by Hospital Corridor	Photoelectric	20458211	
14	Smoke Detector	Basement Corridor by Suite M20	Photoelectric	20458177	
15	Smoke Detector	Basement Corridor by Suite M20	Photoelectric	20458174	
16	Smoke Detector	Basement Above Fire Panel	Photoelectric	36899125	
17	Smoke Detector	Basement Library training room	Photoelectric	20458120	
18	Smoke Detector	Basement Media Center by Stair D	Photoelectric	20458126	
19	Smoke Detector	Basement Media Center by Stair D West	Photoelectric	20458129	
22	Smoke Detector	Basement Public Elevator Foyer	Photoelectric	36899138	
23	Smoke Detector	Basement Staff Elevator M	Photoelectric	20458213	
24	Smoke Detector	Basement Beside Stair	Photoelectric	20458142	
32	Smoke Detector	1st Electrical Closet by Neuroscience Suite 125	Photoelectric	23202108	
33	Smoke Detector	Basement Curtain smoke	Photoelectric	65661852	
34	Smoke Detector	Basement Inside Family Medicine MH647 Storage	Photoelectric	29108019	
1-17	Duct Detector	2nd Mechanical AHU 3 Return	Photoelectric	20458536	
1-18	Duct Detector	2nd Mechanical AHU 3 Supply	Photoelectric	65662161	
2-07	Duct Detector	Penthouse AHU 5 Supply	Photoelectric	20459078	
2-07	Duct Detector	Penthouse AHU 6 Return	Photoelectric	20459077	
2-15	Duct Detector	Penthouse AHU-6 Supply	Photoelectric	20459079	
2-20	Duct Detector	Penthouse AHU 5 Return	Photoelectric	47161097	
15	Pull Station	1st Corridor beside Stairway A	Dual Action	20458436	
24	Pull Station	Basement Inside Electrical rm Outside Entrance	Dual Action	47161093	
26	Pull Station	Basement Electrical rm Outside Entrance	Dual Action	47161095	
027	Smoke Detector	2nd In Optical office	Photoelectric	20458526	
31	Pull Station	Basement vault	Dual Action	20458233	
34	Pull Station	Basement Corridor	Dual Action	20458172	
34	Pull Station	Basement APOGEE	Dual Action	20458155	
34	Pull Station	Penthouse	Dual Action	20459073	
36	Pull Station	Basement Plant Engineering Corridor	Dual Action	20458162	
38	Pull Station	Basement Corridor to Hospital	Dual Action	20458208	
38	Pull Station	Basement Corridor by Digestive Health	Dual Action	20458180	
38	Pull Station	Basement Digestive Health Corridor by Stairwell C	Dual Action	20458206	
40	Pull Station	Basement Digestive Health Corridor	Dual Action	20458185	
47	Pull Station	Basement Media Center by Stair D	Dual Action	20458128	
47	Pull Station	Basement Lab Corridor Stairwell	Dual Action	20458226	
47	Pull Station	1st Corridor infectious disease	Dual Action	20458359	
47	Pull Station	1st Corridor to Hospital	Dual Action	20458337	
47	Pull Station	1st Corridor to Hospital	Dual Action	20458338	
47	Pull Station	1st Corridor to Hospital	Dual Action	20458377	
47	Pull Station	1st Corridor by Neuroscience Suite 125	Dual Action	20458387	
47	Pull Station	1st Corridor in Neuroscience Suite 125	Dual Action	20458408	
47	Pull Station	1st Infusion Center Corridor	Dual Action	20458444	
47	Pull Station	1st Infusion Center Corridor	Dual Action	20458455	
47	Pull Station	1st Oncology Corridor	Dual Action	20458259	
47	Pull Station	1st Oncology Corridor	Dual Action	20458286	
47	Pull Station	1st Performance Improvement Corridor	Dual Action	20458420	
47	Pull Station	1st Performance Improvement Corridor	Dual Action	20458427	
47	Pull Station	1st Staff Elevator Lobby	Dual Action	20458432	
47	Pull Station	1st Suite 190 Corridor	Dual Action	20458329	
50	Pull Station	Basement Corridor	Dual Action	20458141	
54	Pull Station	Basement Corridor	Dual Action	20458135